## FMECA Summary
EQUIPMENT TYPE | FUNCTION | FUNCTION FAILURE | FAILURE MODE | SEVERITY CLASS | FAILURE CODES | FAILURE MODE CHARACTERISTIC | FAILURE CLASSIFICATION | FAILURE EFFECT | FAILURE EFFECT DESCRIPTION | CAUSE | MAINTAINABLE ITEM | POF | COF | RISK | POF | COF | RISK | POF | COF | RISK | POF | COF | RISK | OVERALL RISK RANK | CRITICALITY | FAILURE RATE (PER 1 MILLION HOURS. ) LOWER | FAILURE RATE (PER 1 MILLION HOURS. ) MEAN | FAILURE RATE (PER 1 MILLION HOURS. ) UPPER | NO. OF YEAR / FAILURE | MTTR GENERIC (HOURS) | TOTAL FAILURE RATE (PER 1 MILLION HOURS. ) LOWER | TOTAL FAILURE RATE (PER 1 MILLION HOURS. ) MEAN | TOTAL FAILURE RATE (PER 1 MILLION HOURS. ) UPPER | NO. OF YEAR / FAILURE | MTTR GENERIC (HOURS) | OREDA PAGE NO. | HISTORY START DATE | LAST DATE OF AVAILABLE FAILURE HISTORY | FAILURE (Y/N) | LAST FAILURE DATE | NO. OF FAILURES TO DATE | MTBF-OPERATOR (HOURS) | MTBF-OPERATOR (YEARS) | FAILURE RATE/10^6 HOURS | FAILURE (Y/N) | LAST FAILURE DATE | NO. OF FAILURES TO DATE | MTBF-OPERATOR (YEARS) | FAILURE RATE/10^6 HOURS | STRATEGY DECISION | RECOMMENDATION NAME | RECOMMENDATION DESCRIPTION | CATEGORY | TYPE | RESOURCE | REQUIRED EQUIPMENT STATUS | TIME BASED INTERVAL | TIME BASED INTERVAL (UOME) | REMARKS-4
VALVE, TEMPERATURE RELIEF | TEMPERATURE RELIEF VALVE {EQUIPMENT TAG NUMBER} PROTECT THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} FROM EXCESSIVE PRESSURE OR HEAT THAT MAY CAUSE DAMAGE OR MALFUNCTION. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-PROCESS MEDIUM. | EXTERNAL LEAKAGE-PROCESS MEDIUM | DEGRADED | ELP | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | EXTERNAL LEAKAGE OF TEMPERATURE RELIEF VALVE {EQUIPMENT TAG NUMBER} CAN LEAD TO THE UNWANTED TEMPERATURE ACROSS THE VALVE, WHICH MAY CAUSE DISTURBANCE IN OPERATION AND ENVIRONMENTAL CONSEQUENCES. | LOOSENESS | STEM | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 2 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENT/ACTION TO MITIGATE THE LEAKAGE. CHECK FOR BOLTS TIGHTNESS. REPLACE CONSUMABLES LIKE GASKETS, O-RINGS ETC. (FOR DETAIL, REFER TO PMR) | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, TEMPERATURE RELIEF | TEMPERATURE RELIEF VALVE {EQUIPMENT TAG NUMBER} PROTECT THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} FROM EXCESSIVE PRESSURE OR HEAT THAT MAY CAUSE DAMAGE OR MALFUNCTION. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-UTILITY MEDIUM. | EXTERNAL LEAKAGE-UTILITY MEDIUM | DEGRADED | ELU | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | EXTERNAL LEAKAGE-UTILITY MEDIUM FROM TEMPERATURE RELIEF VALVE {EQUIPMENT TAG NUMBER} MOUNTED ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}, CAN LEAD TO THE ABRUPT/UNWANTED CHANGE IN THE VALVE STATE AND THUS LIMITING THE VALVE TO PERFORM TASK EFFICIENTLY. | MECHANICAL FAILURE-GENERAL | SUBUNIT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 4 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENTS/ACTION TO MITIGATE THE LEAKAGE. REPLACE CONSUMABLES LIKE GASKETS, O RINGS ETC. (FOR DETAIL, REFER TO PMR) | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, TEMPERATURE RELIEF | TEMPERATURE RELIEF VALVE {EQUIPMENT TAG NUMBER} PROTECT THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} FROM EXCESSIVE PRESSURE OR HEAT THAT MAY CAUSE DAMAGE OR MALFUNCTION. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF PLUGGED/CHOKED. | PLUGGED/CHOKED | DEGRADED | PLU | AGE-RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | IF TEMPERATURE RELIEF VALVE {EQUIPMENT TAG NUMBER} PLUGGED/CHOKED DUE TO FOREIGN MATERIAL, IT WOULD NOT WORK PROPERLY AND ULTIMATELY IT WILL LEAD TO PROCESS AT RISK. | BLOCKAGE/PLUGGED | CLOSURE MEMBER (BALL/GATE/DISC/ETC.) | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.12 | 0.76 | 1.86 | 150.1973 | - | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | PERFORM MAJOR OVERHAULING OF THE VALVE, SEAT DISC LAPPING, CLEANING AND SERVICING OF VALVE INTERNALS, AND REPLACEMENT OF ALL SEALS/SOFT GOODS. PERFORM LEAK TEST OF THE VALVE AND ENSURE THAT VALVE CONFORMS TO THE DESIGN VALVE LEAKAGE CLASSIFICATION AS SET OUT IN THE VALVE TAG PLATE OR DATASHEET. ENSURE THE CONTROL VALVE COMPONENTS AND ASSOCIATED CABLING ARE IN GOOD CONDITION, SECURELY FITTED AND FIT FOR PURPOSE. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 36 | MONTH(S)
VALVE, TEMPERATURE RELIEF | TEMPERATURE RELIEF VALVE {EQUIPMENT TAG NUMBER} PROTECT THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} FROM EXCESSIVE PRESSURE OR HEAT THAT MAY CAUSE DAMAGE OR MALFUNCTION. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF VALVE LEAKAGE IN CLOSED POSITION. | VALVE LEAKAGE IN CLOSED POSITION | CRITICAL | LCP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF VALVE LEAKAGE IN CLOSED POSITION OF TEMPERATURE RELIEF VALVE {EQUIPMENT TAG NUMBER} EXCEEDS THAN ACCEPTABLE LEAKAGE RATE, SO IT WOULD NOT BE POSSIBLE TO CONTROL THE OPERATION, WHICH RESULT AS OPERATION DISTURBANCE. | LOOSENESS, CORROSION, INSTRUMENT FAILURE-GENERAL | PACKING, SEAT RINGS, SUBUNIT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 10 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | PERFORM MAJOR OVERHAULING OF THE VALVE, SEAT DISC LAPPING, CLEANING AND SERVICING OF VALVE INTERNALS, AND REPLACEMENT OF ALL SEALS/SOFT GOODS. PERFORM LEAK TEST OF THE VALVE AND ENSURE THAT VALVE CONFORMS TO THE DESIGN VALVE LEAKAGE CLASSIFICATION AS SET OUT IN THE VALVE TAG PLATE OR DATASHEET. ENSURE THE CONTROL VALVE COMPONENTS AND ASSOCIATED CABLING ARE IN GOOD CONDITION, SECURELY FITTED AND FIT FOR PURPOSE. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 36 | MONTH(S)
VALVE, TEMPERATURE RELIEF | TEMPERATURE RELIEF VALVE {EQUIPMENT TAG NUMBER} PROTECT THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} FROM EXCESSIVE PRESSURE OR HEAT THAT MAY CAUSE DAMAGE OR MALFUNCTION. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO REGULATE. | FAIL TO REGULATE | CRITICAL | FTR | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF TEMPERATURE RELIEF VALVE {EQUIPMENT TAG NUMBER} FAIL TO REGULATE, IT WOULD NOT BE POSSIBLE TO CONTROL/KEEP THE OPERATION AT A SET POINT, THIS MAY LEADS TO OPERATION DISTURBANCE. | BLOCKAGE/PLUGGED, INSTRUMENT FAILURE-GENERAL | VALVE BODY W/INTERNALS | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.28 | 1.14 | 2.46 | 100.1316 | 2.7 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT FOR ACTUATOR AND ALL THE TUBING CONNECTIONS FOR UTILITY LEAKAGE AND CHECK POSITIONER FEEDBACK LINK FOR LOOSENESS. ENSURE THAT PROPER INSTRUMENT AIR SUPPLY IS PROVIDING TO POSITIONER AND ACTUATOR AS PER DATA SHEET. ENSURE THAT STEM COUPLING (STEM CONNECTOR) OF ACTUATOR AND VALVE BODY IS TIGHTENED AND PROPERLY ADJUSTED. PERFORM LUBRICATION OF VALVE AND GEARBOX(IF PRESENT). CHECK VALVE TRAVEL IS SAME AS VALVE DATA PLATE. IF THE VALVE STEM TRAVEL INDICATION DIDN’T SHOW CORRECTLY 0% OR 100% TRAVEL AND ANY OFFSET FOUND, PERFORM CALIBRATION OF THE VALVE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 12 | MONTH(S)
ARRESTOR, FLAME | TO ALLOW GAS TO PASS THROUGH IT AND STOPS A FLAME IN ORDER TO PREVENT {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} FROM LARGER FIRE OR EXPLOSION. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF FLAME ARRESTOR {EQUIPMENT TAG NUMBER} MAY CAUSE CATASTROPHIC DAMAGE TO EQUIPMENT, LOSS OF PRODUCTION, INJURY TO PEOPLE AND EVEN LOSS OF LIFE AND POTENTIALLY LARGE LITIGATION COSTS. | FOREIGN PARTICLES, DUSTY ENVIRONMENT | FLAME ARRESTER | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION | REMOVE FLAME ARRESTOR AND INSPECT DEMISTER, REPLACE THE ELEMENT WITH NEW ONE AS PER REQUIREMENT CHECK BOLTED CONNECTION, FLANGES, GASKETS AND ENSURE THERE SHALL BE NO MISSING OR LOOSE BOLTS OR NUTS. ENSURE THERE SHALL BE NO EXCESSIVE MATERIAL LOSS DUE TO DEFORMATION. CLEAN INTERNALLY. MAINTAIN/REPLACE AS PER ITS CONDITION. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
ARRESTOR, FLAME | TO ALLOW GAS TO PASS THROUGH IT AND STOPS A FLAME IN ORDER TO PREVENT {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} FROM LARGER FIRE OR EXPLOSION. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS OF FLAME ARRESTOR {EQUIPMENT TAG NUMBER} MAY CAUSE FAILURE IN OPERATION AND MAY LEAD TO DISASTER. | BLOCKAGE/PLUGGED | FLAME ARRESTER | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION | REMOVE FLAME ARRESTOR AND INSPECT DEMISTER, REPLACE THE ELEMENT WITH NEW ONE AS PER REQUIREMENT CHECK BOLTED CONNECTION, FLANGES, GASKETS AND ENSURE THERE SHALL BE NO MISSING OR LOOSE BOLTS OR NUTS. ENSURE THERE SHALL BE NO EXCESSIVE MATERIAL LOSS DUE TO DEFORMATION. CLEAN INTERNALLY. MAINTAIN/REPLACE AS PER ITS CONDITION. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
VALVE, MASTER | TO ALLOW THE FLOW OR SHUT THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO CLOSE ON DEMAND. | FAIL TO CLOSE ON DEMAND | CRITICAL | FTC | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF MASTER VALVE {EQUIPMENT TAG NUMBER} FAIL TO CLOSE ON DEMAND, IT WOULD NOT BE POSSIBLE TO CONTROL THE PROCESS AND THIS MAY LEAD TO PROCESS DISTURBANCE. | BLOCKAGE/PLUGGED, STICKING, INSTRUMENT FAILURE-GENERAL, MECHANICAL FAILURE-GENERAL, MISCELLANEOUS-GENERAL | VALVE BODY W/INTERNALS, STEM, SUBUNIT, SPRING | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | 0.97 | 5.01 | 117.4804 | 3.8 | 1.3 | 13.57 | 37.01 | 8.4119 | 6.3 | 497 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | PERFORM LUBRICATION/GREASING. CYCLE THE VALVE FULLY OPEN AND CLOSED TO CHECK FOR FREEDOM OF OPERATION. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 4 | YEAR(S)
VALVE, MASTER | TO ALLOW THE FLOW OR SHUT THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO OPEN ON DEMAND. | FAIL TO OPEN ON DEMAND | CRITICAL | FTO | AGE/NON-AGE RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | IF MASTER VALVE {EQUIPMENT TAG NUMBER} FAIL TO OPEN ON DEMAND IT MAY CAUSE PROCESS AND SAFETY CONSEQUENCE. | BLOCKAGE/PLUGGED, CONTROL FAILURE, CORROSION, DEFORMATION, WEAR, STICKING, INSTRUMENT FAILURE-GENERAL, MECHANICAL FAILURE-GENERAL | VALVE COMPONENTS, SUBUNIT | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.0002 | 0.93 | 4.17 | 122.7419 | 5.9 | 1.3 | 13.57 | 37.01 | 8.4119 | 6.3 | 497 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | PERFORM LUBRICATION/GREASING. CYCLE THE VALVE FULLY OPEN AND CLOSED TO CHECK FOR FREEDOM OF OPERATION. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 4 | YEAR(S)
VALVE, MASTER | TO ALLOW THE FLOW OR SHUT THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF VALVE LEAKAGE IN CLOSED POSITION. | VALVE LEAKAGE IN CLOSED POSITION | CRITICAL | LCP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | VALVE LEAKAGE IN CLOSE POSITION WOULD EFFECT THE EFFICIENCY OF MASTER VALVE {EQUIPMENT TAG NUMBER} AND SLIGHTLY IMPACT THE PROCESS. | LOOSENESS, CLEARANCE/ALIGNMENT FAILURE, CORROSION, LEAKAGE, WEAR, INSTRUMENT FAILURE-GENERAL, MATERIAL FAILURE-GENERAL, MECHANICAL FAILURE-GENERAL | VALVE BODY W/INTERNALS, VALVE COMPONENTS, SUBUNIT, SEAT RINGS, PACKING | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.0003 | 0.14 | 0.55 | 815.3571 | 10 | 1.3 | 13.57 | 37.01 | 8.4119 | 6.3 | 497 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY ACTIONS/REPLACEMENT TO MITIGATE THE LEAKAGE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, MASTER | TO ALLOW THE FLOW OR SHUT THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-PROCESS MEDIUM. | EXTERNAL LEAKAGE-PROCESS MEDIUM | CRITICAL | ELP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | EXTERNAL LEAKAGE OF MASTER VALVE {EQUIPMENT TAG NUMBER} WILL LEAD TO SAFETY HAZARD, EXCESSIVE LEAKAGE CAN CAUSE PROCESS INTERRUPTION AS WELL. | CORROSION, LEAKAGE, MECHANICAL FAILURE-GENERAL, MATERIAL FAILURE-GENERAL, LOOSENESS, | BONNET, FLANGE, PACKING, SEALS, SEAT RINGS, STEM, SUBUNIT, VALVE BODY W/INTERNALS | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | 0.36 | 1.88 | 317.0833 | 32 | 1.3 | 13.57 | 37.01 | 8.4119 | 6.3 | 497 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENTS OF GASKETS/PACKINGS/RINGS TO MITIGATE LEAKAGE OR REPLACE VALVE/INTERNALS. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, MASTER | TO ALLOW THE FLOW OR SHUT THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF STRUCTURAL DEFICIENCY. | STRUCTURAL DEFICIENCY | CRITICAL | STD | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | STRUCTURAL DEFICIENCY OF MASTER VALVE {EQUIPMENT TAG NUMBER} WILL CAUSE DEGRADED OPERATION OF VALVE WHICH MAY RESULT IN LEAKAGE IN CLOSED POSITION. THIS MAY ALSO EFFECT THE ISOLATION AS MASTER VALVE WILL NOT ACT PROPERLY DURING SURFACE DISASTER. IT MAY CAUSE THE SAFETY AND ENVIRONMENTAL EFFECTS IN CASE OF EXTERNAL LEAKAGE. | BREAKAGE, CORROSION, INSTRUMENT FAILURE-GENERAL, MATERIAL FAILURE-GENERAL, MISC. EXTERNAL INFLUENCES | BONNET, CABLING & JUNCTION BOXES, CLOSURE MEMBER (BALL/GATE/DISC), PILOT VALVE, VALVE BODY W/INTRNALS | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | 0.17 | 0.93 | 471.4706 | 5 | 1.3 | 13.57 | 37.01 | 8.4119 | 6.3 | 497 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | SHOP INSPECTION/OVERHAULING: PERFORM OVERHAULING OF THE VALVE AT WORKSHOP. A BENCH TEST SHALL BE PERFORMED, HOWEVER, THE VALVE SHALL BE CLEANED OR STEAMED OUT PRIOR TO THE BENCH TEST. ADDITIONALLY, A VISUAL INSPECTION SHALL BE PERFORMED WHERE DETAILED DOCUMENTATION OF THE CONDITION OF THE VALVE INTERNAL COMPONENTS SHALL BE MADE. VISUAL INSPECTION OF DIFFERENT PARTS OF SAFETY VALVE SHALL BE DONE AFTER DISMANTLING TO CHECK THE FOLLOWING: I) CONDITION OF FLANGES FOR PITTING, ROUGHENING, DECREASE IN WIDTH OF SEATING SURFACE ETC. II) SPRING, FOR EVIDENCE OF BENDING, CORROSION OR CRACKING, FREE LENGTH OF SPRING. III) POSITION OF SET SCREWS AND OPENING IN BONNET. IV) INLET/OUTLET NOZZLES FOR EVIDENCE OF DEPOSITS FOREIGN MATERIAL AND CORROSION. V) CONDITION OF EXTERNAL SURFACE AND EVIDENCE OF MECHANICAL DAMAGE. VI) BODY WALL THICKNESS. VII) CONDITIONS OF STEM, GUIDE DISC, NOZZLES ETC. FOR EVIDENCE OF WEAR AND CORROSION. VII) SEATING SURFACE OF DISC AND NOZZLE SHALL BE CRITICALLY EXAMINED FOR ROUGHNESS OR DAMAGE WHICH COULD RESULT IN VALVE LEAKAGE AND MAY NEED CORRECTION. CARE MUST BE TAKEN TO ENSURE FLATNESS OF SEATS. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 4 | YEAR(S)
VALVE, WING | TO CONTROL AND ISOLATE PRODUCTION FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO CLOSE ON DEMAND. | FAIL TO CLOSE ON DEMAND | CRITICAL | FTC | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF WING VALVE {EQUIPMENT TAG NUMBER} FAIL TO CLOSE ON DEMAND, IT WOULD NOT BE POSSIBLE TO CONTROL THE PROCESS AND THIS MAY LEAD TO PROCESS DISTURBANCE. | BLOCKAGE/PLUGGED, STICKING, INSTRUMENT FAILURE-GENERAL, MECHANICAL FAILURE-GENERAL, MISCELLANEOUS-GENERAL | VALVE BODY W/INTERNALS, STEM, SUBUNIT, SPRING | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | 0.97 | 5.01 | 117.4804 | 3.8 | 1.3 | 13.57 | 37.01 | 8.4119 | 6.3 | 497 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | PERFORM LUBRICATION/GREASING. CYCLE THE VALVE FULLY OPEN AND CLOSED TO CHECK FOR FREEDOM OF OPERATION. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 4 | YEAR(S)
VALVE, WING | TO CONTROL AND ISOLATE PRODUCTION FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO OPEN ON DEMAND. | FAIL TO OPEN ON DEMAND | CRITICAL | FTO | AGE/NON-AGE RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | IF WING VALVE {EQUIPMENT TAG NUMBER} FAIL TO OPEN ON DEMAND IT MAY CAUSE PROCESS AND SAFETY CONSEQUENCE. | BLOCKAGE/PLUGGED, CONTROL FAILURE, CORROSION, DEFORMATION, WEAR, STICKING, INSTRUMENT FAILURE-GENERAL, MECHANICAL FAILURE-GENERAL | VALVE COMPONENTS, SUBUNIT | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.0002 | 0.93 | 4.17 | 122.7419 | 5.9 | 1.3 | 13.57 | 37.01 | 8.4119 | 6.3 | 497 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | PERFORM LUBRICATION/GREASING. CYCLE THE VALVE FULLY OPEN AND CLOSED TO CHECK FOR FREEDOM OF OPERATION. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 4 | YEAR(S)
VALVE, WING | TO CONTROL AND ISOLATE PRODUCTION FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF VALVE LEAKAGE IN CLOSED POSITION. | VALVE LEAKAGE IN CLOSED POSITION | CRITICAL | LCP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | VALVE LEAKAGE IN CLOSE POSITION WOULD EFFECT THE EFFICIENCY OF WING VALVE {EQUIPMENT TAG NUMBER} AND SLIGHTLY IMPACT THE PROCESS. | LOOSENESS, CLEARANCE/ALIGNMENT FAILURE, CORROSION, LEAKAGE, WEAR, INSTRUMENT FAILURE-GENERAL, MATERIAL FAILURE-GENERAL, MECHANICAL FAILURE-GENERAL | VALVE BODY W/INTERNALS, VALVE COMPONENTS, SUBUNIT, SEAT RINGS, PACKING | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.0003 | 0.14 | 0.55 | 815.3571 | 10 | 1.3 | 13.57 | 37.01 | 8.4119 | 6.3 | 497 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY ACTIONS/REPLACEMENT TO MITIGATE THE LEAKAGE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, WING | TO CONTROL AND ISOLATE PRODUCTION FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-PROCESS MEDIUM. | EXTERNAL LEAKAGE-PROCESS MEDIUM | CRITICAL | ELP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | EXTERNAL LEAKAGE IN WING VALVE {EQUIPMENT TAG NUMBER} WILL LEAD TO SAFETY HAZARD, EXCESSIVE LEAKAGE CAN CAUSE PROCESS INTERRUPTION AS WELL. | CORROSION, LEAKAGE, MECHANICAL FAILURE-GENERAL, MATERIAL FAILURE-GENERAL, LOOSENESS, | BONNET, FLANGE, PACKING, SEALS, SEAT RINGS, STEM, SUBUNIT, VALVE BODY W/INTERNALS | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | 0.36 | 1.88 | 317.0833 | 32 | 1.3 | 13.57 | 37.01 | 8.4119 | 6.3 | 497 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENTS OF GASKETS/PACKINGS/RINGS TO MITIGATE LEAKAGE OR REPLACE VALVE/INTERNALS. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, WING | TO CONTROL AND ISOLATE PRODUCTION FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF STRUCTURAL DEFICIENCY. | STRUCTURAL DEFICIENCY | CRITICAL | STD | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | STRUCTURAL DEFICIENCY OF WING VALVE {EQUIPMENT TAG NUMBER} WILL CAUSE DEGRADED OPERATION OF VALVE WHICH MAY RESULT IN LEAKAGE IN CLOSED POSITION. THIS MAY ALSO EFFECT THE ISOLATION AS WING VALVE WILL NOT ACT PROPERLY DURING SURFACE DISASTER. IT MAY CAUSE THE SAFETY AND ENVIRONMENTAL EFFECTS IN CASE OF EXTERNAL LEAKAGE. | BREAKAGE, CORROSION, INSTRUMENT FAILURE-GENERAL, MATERIAL FAILURE-GENERAL, MISC. EXTERNAL INFLUENCES | BONNET, CABLING & JUNCTION BOXES, CLOSURE MEMBER (BALL/GATE/DISC), PILOT VALVE, VALVE BODY W/INTRNALS | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | 0.17 | 0.93 | 471.4706 | 5 | 1.3 | 13.57 | 37.01 | 8.4119 | 6.3 | 497 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | SHOP INSPECTION/OVERHAULING: PERFORM OVERHAULING OF THE VALVE AT WORKSHOP. A BENCH TEST SHALL BE PERFORMED, HOWEVER, THE VALVE SHALL BE CLEANED OR STEAMED OUT PRIOR TO THE BENCH TEST. ADDITIONALLY, A VISUAL INSPECTION SHALL BE PERFORMED WHERE DETAILED DOCUMENTATION OF THE CONDITION OF THE VALVE INTERNAL COMPONENTS SHALL BE MADE. VISUAL INSPECTION OF DIFFERENT PARTS OF SAFETY VALVE SHALL BE DONE AFTER DISMANTLING TO CHECK THE FOLLOWING: I) CONDITION OF FLANGES FOR PITTING, ROUGHENING, DECREASE IN WIDTH OF SEATING SURFACE ETC. II) SPRING, FOR EVIDENCE OF BENDING, CORROSION OR CRACKING, FREE LENGTH OF SPRING. III) POSITION OF SET SCREWS AND OPENING IN BONNET. IV) INLET/OUTLET NOZZLES FOR EVIDENCE OF DEPOSITS FOREIGN MATERIAL AND CORROSION. V) CONDITION OF EXTERNAL SURFACE AND EVIDENCE OF MECHANICAL DAMAGE. VI) BODY WALL THICKNESS. VII) CONDITIONS OF STEM, GUIDE DISC, NOZZLES ETC. FOR EVIDENCE OF WEAR AND CORROSION. VII) SEATING SURFACE OF DISC AND NOZZLE SHALL BE CRITICALLY EXAMINED FOR ROUGHNESS OR DAMAGE WHICH COULD RESULT IN VALVE LEAKAGE AND MAY NEED CORRECTION. CARE MUST BE TAKEN TO ENSURE FLATNESS OF SEATS. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 4 | YEAR(S)
VALVE, FLOW CONTROL | TO CONTROL {SERVICE} FLOW BY VARYING THE SIZE OF THE FLOW PASSAGE FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO REGULATE. | FAIL TO REGULATE | CRITICAL | FTR | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF FLOW CONTROL VALVE {EQUIPMENT TAG NUMBER} FAIL TO REGULATE, IT WOULD NOT BE POSSIBLE TO CONTROL/KEEP THE PROCESS AT A SET POINT, THIS MAY LEADS TO PROCESS DISTURBANCE. | BLOCKAGE/PLUGGED, INSTRUMENT FAILURE-GENERAL | VALVE BODY W/INTERNALS | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.28 | 1.14 | 2.46 | 100.1316 | 2.7 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT FOR ACTUATOR AND ALL THE TUBING CONNECTIONS FOR UTILITY LEAKAGE AND CHECK POSITIONER FEEDBACK LINK FOR LOOSENESS. ENSURE THAT PROPER INSTRUMENT AIR SUPPLY IS PROVIDING TO POSITIONER AND ACTUATOR AS PER DATA SHEET. ENSURE THAT STEM COUPLING (STEM CONNECTOR) OF ACTUATOR AND VALVE BODY IS TIGHTENED AND PROPERLY ADJUSTED. PERFORM LUBRICATION OF VALVE AND GEARBOX(IF PRESENT). CHECK VALVE TRAVEL IS SAME AS VALVE DATA PLATE. IF THE VALVE STEM TRAVEL INDICATION DIDN’T SHOW CORRECTLY 0% OR 100% TRAVEL AND ANY OFFSET FOUND, PERFORM CALIBRATION OF THE VALVE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 12 | MONTH(S)
VALVE, FLOW CONTROL | TO CONTROL {SERVICE} FLOW BY VARYING THE SIZE OF THE FLOW PASSAGE FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-PROCESS MEDIUM. | EXTERNAL LEAKAGE-PROCESS MEDIUM | DEGRADED | ELP | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | EXTERNAL LEAKGE OF FLOW CONTROL VALVE {EQUIPMENT TAG NUMBER} CAN LEAD TO THE UNWANTED PRESSURE DROP ACROSS THE VALVE, WHICH MAY CAUSE DISTURBANCE IN OPERATION AND ENVIRONMENTAL CONSEQUENCES MAY HAPPEN. | LOOSENESS | STEM | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 2 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENT/ACTION TO MITIGATE THE LEAKAGE. CHECK FOR BOLTS TIGHTNESS. REPLACE CONSUMABLES LIKE GASKETS, O-RINGS ETC. (FOR DETAIL, REFER TO PMR) | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, FLOW CONTROL | TO CONTROL {SERVICE} FLOW BY VARYING THE SIZE OF THE FLOW PASSAGE FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-UTILITY MEDIUM. | EXTERNAL LEAKAGE-UTILITY MEDIUM | DEGRADED | ELU | NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | EXTERNAL LEAKAGE-UTILITY MEDIUM CAN LEAD TO THE ABRUPT/UNWANTED CHANGE IN THE FLOW CONTROL VALVE {EQUIPMENT TAG NUMBER} STATE AND THUS LIMITING THE VALVE TO PERFORM TASK EFFICIENTLY. | MECHANICAL FAILURE-GENERAL | SUBUNIT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 4 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENTS/ACTION TO MITIGATE THE LEAKAGE. REPLACE CONSUMABLES LIKE GASKETS, O RINGS ETC. (FOR DETAIL, REFER TO PMR) | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, FLOW CONTROL | TO CONTROL {SERVICE} FLOW BY VARYING THE SIZE OF THE FLOW PASSAGE FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF PLUGGED/CHOKED. | PLUGGED/CHOKED | DEGRADED | PLU | AGE-RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | IF FLOW CONTROL VALVE {EQUIPMENT TAG NUMBER} PLUGGED/CHOKED DUE TO FOREIGN MATERIAL, IT WOULD NOT WORK PROPERLY AND ULTIMATELY IT WILL LEAD TO PROCESS AT RISK. | BLOCKAGE/PLUGGED | CLOSURE MEMBER (BALL/GATE/DISC/ETC.) | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.12 | 0.76 | 1.86 | 150.1973 | - | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | PERFORM MAJOR OVERHAULING OF THE VALVE, SEAT DISC LAPPING, CLEANING AND SERVICING OF VALVE INTERNALS, AND REPLACEMENT OF ALL SEALS/SOFT GOODS. PERFORM LEAK TEST OF THE VALVE AND ENSURE THAT VALVE CONFORMS TO THE DESIGN VALVE LEAKAGE CLASSIFICATION AS SET OUT IN THE VALVE TAG PLATE OR DATASHEET. ENSURE THE CONTROL VALVE COMPONENTS AND ASSOCIATED CABLING ARE IN GOOD CONDITION, SECURELY FITTED AND FIT FOR PURPOSE. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 36 | MONTH(S)
VALVE, FLOW CONTROL | TO CONTROL {SERVICE} FLOW BY VARYING THE SIZE OF THE FLOW PASSAGE FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF VALVE LEAKAGE IN CLOSED POSITION. | VALVE LEAKAGE IN CLOSED POSITION | CRITICAL | LCP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF VALVE LEAKAGE IN CLOSED POSITION OF FLOW CONTROL VALVE {EQUIPMENT TAG NUMBER} EXCEEDS THAN ACCEPTABLE LEAKAGE RATE, SO IT WOULD NOT BE POSSIBLE TO CONTROL THE PROCESS, WHICH RESULT AS PROCESS DISTURBANCE. | LOOSENESS, CORROSION, INSTRUMENT FAILURE-GENERAL | PACKING, SEAT RINGS, SUBUNIT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 10 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | PERFORM MAJOR OVERHAULING OF THE VALVE, SEAT DISC LAPPING, CLEANING AND SERVICING OF VALVE INTERNALS, AND REPLACEMENT OF ALL SEALS/SOFT GOODS. PERFORM LEAK TEST OF THE VALVE AND ENSURE THAT VALVE CONFORMS TO THE DESIGN VALVE LEAKAGE CLASSIFICATION AS SET OUT IN THE VALVE TAG PLATE OR DATASHEET. ENSURE THE CONTROL VALVE COMPONENTS AND ASSOCIATED CABLING ARE IN GOOD CONDITION, SECURELY FITTED AND FIT FOR PURPOSE. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 36 | MONTH(S)
VALVE, MOTOR OPERATED | TO CONTROL FLUID FLOW BY VARYING THE SIZE OF THE FLOW PASSAGE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF EXTERNAL LEAKAGE-PROCESS MEDIUM. | EXTERNAL LEAKAGE-PROCESS MEDIUM | DEGRADED | ELP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | EXTERNAL LEAKAGE-PROCESS MEDIUM OF MOTOR OPERATED VALVE {EQUIPMENT TAG NUMBER} ON DISCHARGE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} MAY AFFECT SUPPLY OF {SERVICE}, WHICH MAY HAVE IMPACT ON SYSTEM EFFICIENCY. | LOOSENESS | STEM | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 2 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | PERFORM NECESSARY REPLACEMENT / ACTION TO MITIGATE THE LEAKAGE. CHECK FOR BOLTS TIGHTNESS. REPLACE CONSUMABLES LIKE GASKETS , O-RINGS ETC. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 6 | MONTH(S)
VALVE, MOTOR OPERATED | TO CONTROL FLUID FLOW BY VARYING THE SIZE OF THE FLOW PASSAGE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE WILL OCCURE IN CASE OF FAIL TO CLOSE ON DEMAND. | FAIL TO CLOSE ON DEMAND | CRITICAL | FTC | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | FAIL TO CLOSE ON DEMAND OF MOTOR OPERATED VALVE {EQUIPMENT TAG NUMBER} ON DISCHARGE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL AFFECT SUPPLY OF {SERVICE}, WHICH MAY HAVE IMPACT ON SYSTEM EFFICIENCY. | BLOCKAGE/PLUGGED | CLOSURE MEMBER (BALL/GATE/DISC/ETC.) | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 2 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CHECK FOR THE INTERLOCKS OF VALVE OPERATION IF ANY. CHECK THE INTEGRITY OF ALL THE ASSOCIATED INSTRUMENTATION. ENSURE THE VALVE COMPONENTS AND ASSOCIATED CONTROL LINE IS IN GOOD CONDITION, SECURELY FITTED, NOT LEAKING AND FIT FOR PURPOSE. CHECK THAT PROPER VOLTAGES IS GIVING TO VALVE POSITIONER AND LIMIT SWITCHES. ENSURE THAT CONTROL SYSTEM IS SHOWING CORRECT INDICATION OF VALVE ACCESSORIES. PERFORM LUBRICATION OF VALVE AND GEARBOX(IF PRESENT). CHECK VALVE TRAVEL IS SAME AS VALVE DATA PLATE. CHECK THE LIMIT OR POSITION SWITCH FUNCTIONALITY BY USING MILLIMETER. CHECK FOR LOOSENESS OR LEAKAGE FROM ACTUATOR OR CONTROL TUBING CHECK PROPER OPERATION OF THE ASSOCIATED MOTOR. | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 6 | MONTH(S)
VALVE, MOTOR OPERATED | TO CONTROL FLUID FLOW BY VARYING THE SIZE OF THE FLOW PASSAGE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE WILL OCCURE IN CASE OF FAIL TO OPEN ON DEMAND. | FAIL TO OPEN ON DEMAND | CRITICAL | FTO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | FAIL TO OPEN ON DEMAND OF MOTOR OPERATED VALVE {EQUIPMENT TAG NUMBER} ON DISCHARGE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL AFFECT SUPPLY OF {SERVICE}, WHICH MAY HAVE IMPACT ON SYSTEM EFFICIENCY. | DEFORMATION, INSTRUMENT FAILURE GENERAL | POSITIONER, SUBUNIT | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.12 | 0.76 | 1.86 | 150.1973 | 1.8 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CHECK THE INTEGRITY OF ALL THE ASSOCIATED INSTRUMENTATION SUCH AS LIMIT SWITCHES AND SOLENOID VALVES. ENSURE FOR PROPER SUPPLY VOLTAGES TO THE ASSOCIATED ACCESSORIES. CHECK FOR LOOSENESS OR LEAKAGE FROM ACTUATOR OR CONTROL TUBING. ENSURE PROPER WORKING OF ASSOCIATED INSTRUMENTATION OF VALVE PERFORM LUBRICATION OF VALVE AND GEARBOX(IF PRESENT). CHECK FOR THE INTERLOCKS OF VALVE IF ANY. ENSURE VALVE INDICATION ON THE CONTROL PANEL IS CORRECT. CHECK THE CONTROL PANEL FOR ANY ABNORMALITY. ENSURE THAT PROPER PNEUMATIC SUPPLY IS PROVIDING TO THE VALVE. CHECK THE VALVE BODY FOR ANY DAMAGE AND CORROSION. CHECK IF THE BUG SCREEN IS IN TACT AND THAT THE VENT PORT IS NOT CLOGGED WITH ANY FOREIGN MATERIAL. ENSURE THE PROPER FUNCTION OF THE ASSOCIATED MOTOR. | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 6 | MONTH(S)
VALVE, MOTOR OPERATED | TO CONTROL FLUID FLOW BY VARYING THE SIZE OF THE FLOW PASSAGE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE WILL OCCURE IN CASE OF FAIL TO REGULATE. | FAIL TO REGULATE | CRITICAL | FTR | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | FAIL TO REGULATE OF MOTOR OPERATED VALVE {EQUIPMENT TAG NUMBER} ON DISCHARGE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL AFFECT SUPPLY OF {SERVICE}, WHICH MAY HAVE IMPACT ON SYSTEM EFFICIENCY. | BLOCKAGE/ PLUGGED, INSTRUMENT FAILURE GENERAL | VALVE BODY WITH INTERNALS | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.28 | 1.14 | 2.46 | 100.1316 | 2.7 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT, MOH | PREVENTIVE MAINTENANCE TASK, MAJOR OVERHAULING | PREVENTIVE MAINTENANCE: VISUALLY INSPECT FOR VALVE FOR ANY DAMAGES AND DEGRADATION. CHECK TUBING CONNECTIONS FOR UTILITY LEAKAGE CHECK POSITIONER FEEDBACK LINK FOR LOOSENESS. ENSURE THAT PROPER INSTRUMENT AIR SUPPLY IS PROVIDING TO POSITIONER AND ACTUATOR AS PER DATA SHEET. ENSURE THAT STEM COUPLING (STEM CONNECTOR) OF ACTUATOR AND VALVE BODY IS TIGHTENED AND PROPERLY ADJUSTED. CHECK VALVE TRAVEL IS SAME AS VALVE DATA PLATE. IF THE VALVE STEM TRAVEL INDICATION DIDN’T SHOW CORRECTLY 0% OR 100% TRAVEL AND ANY OFFSET FOUND, PERFORM CALIBRATION OF THE VALVE. MAJOR OVERHAULING: REMOVE YOKE ASSEMBLY FROM THE VALVE. ISOLATE THE VALVE STEM. CHECK THE VALVE INTERNALS. OVERHAUL THE VALVE AS PER PROCEDURE. | PMT-PREVENTIVE MAINTENANCE TASK, PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK, PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN, MAINT-MAINTENANCE TECHNICIAN | OFF, OFF | 6, 18 | MONTH(S), MONTH(S)
VALVE, MOTOR OPERATED | TO CONTROL FLUID FLOW BY VARYING THE SIZE OF THE FLOW PASSAGE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF VALVE LEAKAGE IN CLOSED POSITION. | VALVE LEAKAGE IN CLOSED POSITION | CRITICAL | LCP | AGE/NON-AGE RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | VALVE LEAKAGE IN CLOSED POSITION OF MOTOR OPERATED VALVE {EQUIPMENT TAG NUMBER} ON DISCHARGE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} MAY AFFECT SUPPLY OF {SERVICE}, WHICH MAY HAVE IMPACT ON SYSTEM EFFICIENCY. | CORROSION, LOOSENESS, INSTRUMENT FAILURE GENERAL | PACKING, SEAT RINGS, SUBUNIT | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 10 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | PERFORM MAJOR OVERHAULING OF THE VALVE, SEAT DISC LAPPING, CLEANING AND SERVICING OF VALVE INTERNALS, AND REPLACEMENT OF ALL SEALS/SOFT GOODS. PERFORM LEAK TEST OF THE VALVE AND ENSURE THAT VALVE CONFORMS TO THE DESIGN VALVE LEAKAGE CLASSIFICATION AS SET OUT IN THE VALVE TAG PLATE OR DATASHEET. ENSURE THE VALVE COMPONENTS AND ASSOCIATED CABLING ARE IN GOOD CONDITION, SECURELY FITTED AND FIT FOR PURPOSE. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 18 | MONTH(S)
VALVE, CONTROL ON/OFF | TO CONTROL FLUID FLOWRATE BY VARYING THE SIZE OF THE FLOW PASSAGE ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO CLOSE ON DEMAND. | FAIL TO CLOSE ON DEMAND | CRITICAL | FTC | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF ON/OFF CONTROL VALVE {EQUIPMENT TAG NUMBER} FAIL TO CLOSE ON DEMAND, IT WOULD NOT BE POSSIBLE TO CONTROL/KEEP THE PROCESS AT A SET POINT, THIS MAY LEADS TO PROCESS DISTURBANCE. | BLOCKAGE/PLUGGED, INSTRUMENT FAILURE GENERAL, MECHANICAL FAILURE GENERAL, STICKING | PILOT VALVE, STEM, VALVE BODY WITH INTERNALS, SUBUNIT | 5 | E | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | 2.27 | 11.88 | 50.2863 | 2.8 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | CHECK THE INTEGRITY OF ALL THE ASSOCIATED INSTRUMENTATION SUCH AS LIMIT SWITCHES AND SOLENOID VALVES. CHECK FOR PROCESS LEAKAGE FROM VALVE BODY, VALVE STEM AND PIPE FLANGES. CHECK THAT PROPER VOLTAGES IS GIVING TO SOLENOID VALVE AND LIMIT SWITCHES. ENSURE THAT CONTROL SYSTEM IS SHOWING CORRECT INDICATION OF VALVE STATUS. PERFORM LUBRICATION OF VALVE AND GEARBOX(IF PRESENT). CHECK VALVE TRAVEL IS SAME AS VALVE DATA PLATE/DATASHEET. CHECK FOR THE INTERLOCKS OF VALVE OPERATION IF ANY. ENSURE THE VALVE COMPONENTS AND ASSOCIATED CONTROL LINE IS IN GOOD CONDITION, SECURELY FITTED. CHECK FOR ANY ABNORMAL INDICATION ON CONTROL PANEL. PERFORM PARTIAL FUNCTION TEST AND OVERHAUL. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
VALVE, CONTROL ON/OFF | TO CONTROL FLUID FLOWRATE BY VARYING THE SIZE OF THE FLOW PASSAGE ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-UTILITY MEDIUM. | EXTERNAL LEAKAGE-UTILITY MEDIUM | DEGRADED | ELU | NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | EXTERNAL LEAKAGE-UTILITY MEDIUM CAN LEAD TO THE ABRUPT/UNWANTED CHANGE IN THE ON/OFF CONTROL VALVE {EQUIPMENT TAG NUMBER} STATE AND THUS LIMITING THE VALVE TO PERFORM TASK EFFICIENTLY. | LEAKAGE, MECHANICAL FAILURE-GENERAL | SEALS, SEALS GASKET | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.004 | 0.24 | 0.76 | 475.425 | 2 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | PERFORM NECESSARY REPLACEMENTS/ACTION TO MITIGATE THE LEAKAGE. CHECK FOR ANY CORROSION AND LEAKAGE IN THE UTILITY TUBING AND RECTIFY/REPLACE IF REQUIRED. REPLACE CONSUMABLES LIKE GASKETS, O RINGS, INSTRUMENT AIR TUBING ETC. TIGHTEN THE PROCESS CONNECTIONS OR FASTENERS. | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 1 | YEAR(S)
VALVE, CONTROL ON/OFF | TO CONTROL FLUID FLOWRATE BY VARYING THE SIZE OF THE FLOW PASSAGE ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | SPURIOUS OPERATION OF ON/OFF CONTROL VALVE {EQUIPMENT TAG NUMBER} MAY LEAD TO UNWANTED CHANGE IN THE STATE OF ITS CORRSPONDING EQUIPMENT, THIS MAY LEAD TO PROCESS DISTURBANCE. | MECHANICAL FAILURE-GENERAL | SUBUNIT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | 0.28 | 1.4 | 407.4786 | 6 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CHECK FOR THE INTERLOCKS OF VALVE OPERATION IF ANY. ENSURE THE VALVE COMPONENTS AND ASSOCIATED CONTROL LINE IS IN GOOD CONDITION, SECURELY FITTED, NOT LEAKING AND FIT FOR PURPOSE. INSPECT THE PROPER WORKING OF ALL ASSOCIATED INSTRUMENTATION. CHECK ALL THE ACCESSORIES FOR DAMAGE OR DEGRADATION. CHECK ELECTRIC AND OTHER UTILITIES ARE ADEQUATE FOR THE VALVE AND ACCESSORIES. CHECK FOR ALL TERMINALS INTEGRITY AND TIGHTEN ANY LOOSE TERMINALS. | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 1 | YEAR(S)
VALVE, CONTROL ON/OFF | TO CONTROL FLUID FLOWRATE BY VARYING THE SIZE OF THE FLOW PASSAGE ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF VALVE LEAKAGE IN CLOSED POSITION. | VALVE LEAKAGE IN CLOSED POSITION | CRITICAL | LCP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF VALVE LEAKAGE IN CLOSED POSITION OF ON/OFF CONTROL VALVE {EQUIPMENT TAG NUMBER} EXCEEDS THAN ACCEPTABLE LEAKAGE RATE, SO IT WOULD NOT BE POSSIBLE TO CONTROL THE PROCESS, WHICH RESULT AS PROCESS DISTURBANCE. | LEAKAGE, WEAR | SEALS, VALVE BODY WITH INTERNALS | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | 0.34 | 1.88 | 335.7353 | - | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | ENSURE THE VALVE COMPONENTS AND ASSOCIATED CABLING, PIPING ETC. ARE IN GOOD CONDITION, SECURELY FITTED AND FIT FOR PURPOSE. CHECK FOR PROCESS LEAKAGE FROM VALVE BODY, VALVE STEM AND PIPE FLANGES. CHECK EQUIPMENT AND ACCESSORIES TAGS FOR SOUNDNESS AND CHECK THAT VIBRATION IS NOT AFFECTING INTEGRITY. CHECK ALL THE ACCESSORIES FOR DAMAGE OR DEGRADATION. PERFORM PARTIAL FUNCTION TEST AND OVERHAUL | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 1 | YEAR(S)
VALVE, CONTROL ON/OFF | TO CONTROL FLUID FLOWRATE BY VARYING THE SIZE OF THE FLOW PASSAGE ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO OPEN ON DEMAND. | FAIL TO OPEN ON DEMAND | CRITICAL | FTO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | IF ON/OFF CONTROL VALVE {EQUIPMENT TAG NUMBER} FAIL TO OPEN ON DEMAND, IT WOULD NOT BE POSSIBLE TO CONTROL/KEEP THE PROCESS AT A SET POINT, THIS MAY LEADS TO PROCESS DISTURBANCE. | BLOCKAGE/PLUGGED, INSTRUMENT FAILURE GENERAL, MECHANICAL FAILURE GENERAL | PILOT VALVE, SUBUNIT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 1.08 | 3.46 | 105.4944 | 2.3 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CHECK THE INTEGRITY OF ALL THE ASSOCIATED INSTRUMENTATION SUCH AS LIMIT SWITCHES AND SOLENOID VALVES. ENSURE FOR PROPER SUPPLY VOLTAGES TO SOLENOID VALVE. CHECK FOR LOOSENESS OR LEAKAGE FROM ACTUATOR OR CONTROL TUBING. ENSURE PROPER WORKING OF ASSOCIATED INSTRUMENTATION OF VALVE VISUALLY CHECK FOR ALL THE TUBING CONNECTIONS FOR LOOSENESS. ENSURE VALVE STATUS INDICATION ON THE CONTROL PANEL IS CORRECT PERFORM FUNCTION TEST OF SOLENOID VALVE. CONFIRM ASSOCIATED ALARMS AND EXECUTIVE ACTIONS/INTERLOCKS OPERATE SATISFACTORILY. ON COMPLETION OF FUNCTION TEST, CHECK ALARMS AND ANNUNCIATIONS ARE EXTINGUISHED. IF ANY OF THE ABOVE TESTS ARE UNSATISFACTORY, REMEDIAL ACTION SHOULD BE TAKEN, CARRY OUT AN OVERHAUL IN ACCORDANCE WITH RELEVANT PROCEDURES AND FUNCTION TEST VALVE ON COMPLETION (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 1 | YEAR(S)
VALVE, SOLENOID | TO CONTROL THE FLOW OF {SERVICE} ON THE OUTLET OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO OPEN ON DEMAND. | FAIL TO OPEN ON DEMAND | CRITICAL | FTO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | IF SOLENOID CONTROL VALVE {EQUIPMENT TAG NUMBER} FAIL TO OPEN ON DEMAND IT WILL EFFECT THE PERFORMANCE OF PRESSURE CONTROL VALVE. | BLOCKAGE/PLUGGED, CONTROL FAILURE, CORROSION, DEFORMATION, WEAR, STICKING, INSTRUMENT FAILURE-GENERAL, MECHANICAL FAILURE-GENERAL | MONITORING, VALVE COMPONENTS, SUBUNIT, PILOT VALVE, POSITIONER | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.0002 | 0.93 | 4.17 | 122.7419 | 5.9 | 1.3 | 13.57 | 37.01 | 8.4119 | 6.3 | 497 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT ALL THE TUBING CONNECTIONS FOR AIR LEAKAGE. CHECK THE VALVE BODY FOR ANY DAMAGE AND CORROSION. CHECK IF THE BUG SCREEN IS IN TACT AND THAT THE VENT PORT IS NOT CLOGGED WITH ANY FOREIGN MATERIAL. MAKE SURE THAT THE SOV COIL IS ENERGIZED OR DE-ENERGIZED AS PER ITS NORMAL STATE. PERFORM THE FUNCTION TEST OF SOLENOID WITH ASSOCIATED EQUIPMENT AND ENSURE IT'S PROPER WORKING. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
VALVE, SOLENOID | TO CONTROL THE FLOW OF {SERVICE} ON THE OUTLET OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF INTERNAL LEAKAGE. | INTERNAL LEAKAGE | CRITICAL | INL | NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | INTERNAL LEAKAGE OF SOLENOID CONTROL VALVE {EQUIPMENT TAG NUMBER} MAY EFFECT THE OPERATION OF PRESSURE CONTROL VALVE. | LEAKAGE, MATERIAL FAILURE-GENERAL, MECHANICAL FAILURE-GENERAL | CLOSURE MEMBER (BALL/GATE/DISC/ETC.), ACTUATOR COMPONENTS, PACKING, SEALS (GASKETS), SUBUNIT | 3 | E | RISK RANK 4 | 3 | D | RISK RANK 3 | 3 | E | RISK RANK 4 | 3 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.0005 | 0.11 | 0.42 | 1037.7273 | 6.3 | 1.3 | 13.57 | 37.01 | 8.4119 | 6.3 | 497 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT ALL THE TUBING CONNECTIONS FOR AIR LEAKAGE. MAKE SURE THAT THE SOV COIL IS ENERGIZED OR DE-ENERGIZED AS PER ITS NORMAL STATE. ENSURE THAT PORT IS NOT CHOCKED. IF STILL INTERNAL LEAKAGE NOT RESOLVED, REPLACE THE SOLENOID VALVE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
VALVE, SOLENOID | TO CONTROL THE FLOW OF {SERVICE} ON THE OUTLET OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO CLOSE ON DEMAND. | FAIL TO CLOSE ON DEMAND | CRITICAL | FTC | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF SOLENOID VALVE {EQUIPMENT TAG NUMBER} FAIL TO CLOSE ON DEMAND, IT MAY EFFECT THE OPERATION OF PRESSURE CONTROL VALVE. | BLOCKAGE/PLUGGED, STICKING, INSTRUMENT FAILURE-GENERAL, MECHANICAL FAILURE-GENERAL, MISCELLANEOUS-GENERAL | CLOSURE MEMBER (BALL/GATE/DISC/ETC.), PILOT VALVE, SPRING, VALVE BODY W/INTERNALS, STEM, SUBUNIT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | 0.97 | 5.01 | 117.4804 | 3.8 | 1.3 | 13.57 | 37.01 | 8.4119 | 6.3 | 497 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT ALL THE TUBING CONNECTIONS FOR AIR LEAKAGE. MAKE SURE THAT THE SOV COIL IS ENERGIZED OR DE-ENERGIZED AS PER ITS NORMAL STATE. ENSURE THAT PORT IS NOT CHOCKED. IF STILL INTERNAL LEAKAGE NOT RESOLVED, REPLACE THE SOLENOID VALVE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
VALVE, SOLENOID | TO CONTROL THE FLOW OF {SERVICE} ON THE OUTLET OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF VALVE LEAKAGE IN CLOSED POSITION. | VALVE LEAKAGE IN CLOSED POSITION | CRITICAL | LCP | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF SOLENOID CONTROL VALVE {EQUIPMENT TAG NUMBER} HAS LEAKAGE IN CLOSE POSITION MAY CAUSE UNWANTED CHANGE IN THE OPERATION OF PRESSURE CONTROL VALVE. | LOOSENESS, CLEARANCE/ALIGNMENT FAILURE, CORROSION, LEAKAGE, WEAR, INSTRUMENT FAILURE-GENERAL, MATERIAL FAILURE-GENERAL, MECHANICAL FAILURE-GENERAL | VALVE BODY W/INTERNALS, VALVE COMPONENTS, SUBUNIT, SEAT RINGS, PACKING | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.0003 | 0.14 | 0.55 | 815.3571 | 10 | 1.3 | 13.57 | 37.01 | 8.4119 | 6.3 | 497 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT ALL THE TUBING CONNECTIONS FOR AIR LEAKAGE. MAKE SURE THAT THE SOV COIL IS ENERGIZED OR DE-ENERGIZED AS PER ITS NORMAL STATE. ENSURE THAT PORT IS NOT CHOCKED. IF STILL INTERNAL LEAKAGE NOT RESOLVED, REPLACE THE SOLENOID VALVE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
VALVE, SOLENOID | TO CONTROL THE FLOW OF {SERVICE} ON THE OUTLET OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF SOLENOID CONTROL VALVE {EQUIPMENT TAG NUMBER} MAY CAUSE UNWANTED CHANGE IN THE STATE OF PRESSURE CONTROL VALVE. IT MAY ALSO EFFECT ON PROCESS. | MECHANICAL FAILURE-GENERAL | SUBUNIT | 3 | F | RISK RANK 4 | 3 | D | RISK RANK 3 | 3 | E | RISK RANK 4 | 3 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | 0.08 | 0.44 | 1426.875 | 6 | 1.3 | 13.57 | 37.01 | 8.4119 | 6.3 | 497 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT ALL THE TUBING CONNECTIONS FOR AIR LEAKAGE. MAKE SURE THAT THE SOV COIL IS ENERGIZED OR DE-ENERGIZED AS PER ITS NORMAL STATE. ENSURE THAT PORT IS NOT CHOCKED. IF STILL INTERNAL LEAKAGE NOT RESOLVED, REPLACE THE SOLENOID VALVE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
VALVE, BLOWDOWN | TO CONTROL THE FLOW OF FLUID {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-PROCESS MEDIUM. | EXTERNAL LEAKAGE-PROCESS MEDIUM | CRITICAL | ELP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | EXTERNAL LEAKAGE OF BLOWDOWN VALVE {EQUIPMENT TAG NUMBER} CAN LEAD TO THE UNWANTED PRESSURE DROP ACROSS THAT VALVE, PROCESS AND SAFETY RELATED CONSEQUENCES MAY OCCUR. | CORROSION, LEAKAGE, MECHANICAL FAILURE-GENERAL | BONNET, SEAT RINGS, STEM, SUBUNIT, PACKING, SEALS | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.05 | 1.12 | 3.37 | 101.9194 | 32 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENTS/ACTION TO MITIGATE THE LEAKAGE. CHECK FOR BOLTS TIGHTNESS. REPLACE CONSUMABLES LIKE GASKETS, O-RINGS ETC. (FOR DETAIL, REFER TO PMR) | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, BLOWDOWN | TO CONTROL THE FLOW OF FLUID {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-UTILITY MEDIUM. | EXTERNAL LEAKAGE-UTILITY MEDIUM | DEGRADED | ELU | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | EXTERNAL LEAKAGE-UTILITY MEDIUM CAN LEAD TO THE ABRUPT/UNWANTED CHANGE IN THE BLOWDOWN VALVE {EQUIPMENT TAG NUMBER} STATE AND THUS LIMITING THE VALVE TO PERFORM TASK EFFICIENTLY. | LEAKAGE, MECHANICAL FAILURE-GENERAL | SEALS, SEALS GASKET | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.004 | 0.24 | 0.76 | 475.425 | 2 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENTS/ACTION TO MITIGATE THE LEAKAGE. REPLACE CONSUMABLES LIKE GASKETS, O RINGS ETC. (FOR DETAIL, REFER TO PMR) | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, BLOWDOWN | TO CONTROL THE FLOW OF FLUID {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO CLOSE ON DEMAND. | FAIL TO CLOSE ON DEMAND | CRITICAL | FTC | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF BLOWDOWN VALVE {EQUIPMENT TAG NUMBER} FAIL TO CLOSE ON DEMAND IT WOULD NOT BE ABLE TO CONTROL THE DESIRED PROCESS ARE REQUIREMENTS, AN OPERATIONAL EFFECT MAY OCCUR DUE TO THIS FAILURE. | BLOCKAGE/PLUGGED, STICKING, INSTRUMENT FAILURE-GENERAL, MECHANICAL FAILURE-GENERAL | VALVE BODY W/INTERNALS, PILOT VALVE, STEM, SUBUNIT, SEAT RINGS | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | 2.27 | 11.88 | 50.2863 | 2.8 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CHECK THE INTEGRITY OF ALL THE ASSOCIATED INSTRUMENTATION. CHECK THAT PROPER VOLTAGES IS GIVING TO ALL ASSOCIATED INSTRUMENTATION. ENSURE THAT CONTROL SYSTEM IS SHOWING CORRECT INDICATION OF VALVE ACCESSORIES. PERFORM LUBRICATION OF VALVE AND GEARBOX(IF PRESENT). CHECK VALVE TRAVEL IS SAME AS VALVE DATA PLATE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
VALVE, BLOWDOWN | TO CONTROL THE FLOW OF FLUID {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO OPEN ON DEMAND. | FAIL TO OPEN ON DEMAND | CRITICAL | FTO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | IF BLOWDOWN VALVE {EQUIPMENT TAG NUMBER} FAIL TO OPEN ON DEMAND THEN IT WOULD NOT BE ABLE TO GIVE SUPPLY OF {SERVICE}, WHICH MAY LEADS TO THE OPERATIONAL CONSEQUENCE. | BLOCKAGE/PLUGGED, INSTRUMENT FAILURE-GENERAL, MECHANICAL FAILURE-GENERAL | PILOT VALVE, SUBUNIT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 1.08 | 3.46 | 105.4944 | 2.3 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CHECK THE INTEGRITY OF ALL THE ASSOCIATED INSTRUMENTATION. VISUALLY CHECK FOR ALL THE TUBING CONNECTIONS FOR LOOSENESS. PERFORM LUBRICATION OF VALVE AND GEARBOX(IF PRESENT). ENSURE THE PROPER SUPPLY VOLTAGES. ENSURE VALVE INDICATION ON THE DCS IS CORRECT. (FOR DETAILS REFER PMR). | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
VALVE, BLOWDOWN | TO CONTROL THE FLOW OF FLUID {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF THE BLOWDOWN VALVE {EQUIPMENT TAG NUMBER} MAY CAUSE PROCESS AND SAFETY HAZARD. | MECHANICAL FAILURE-GENERAL | SUBUNIT | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | 0.28 | 1.4 | 407.4786 | 6 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CHECK FOR THE INTERLOCKS OF VALVE OPERATION IF ANY. ENSURE THE VALVE COMPONENTS AND ASSOCIATED CABLING, PIPING ETC. ARE IN GOOD CONDITION, SECURELY FITTED, NOT LEAKING AND FIT FOR PURPOSE. INSPECT THE PROPER WORKING OF ALL ASSOCIATED INSTRUMENTATION. CHECK ALL THE ACCESSORIES FOR DAMAGE OR DEGRADATION. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
VALVE, BLOWDOWN | TO CONTROL THE FLOW OF FLUID {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF VALVE LEAKAGE IN CLOSED POSITION. | VALVE LEAKAGE IN CLOSED POSITION | CRITICAL | LCP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | VALVE LEAKAGE IN CLOSE POSITION OF THE BLOWDOWN VALVE {EQUIPMENT TAG NUMBER} MAY CAUSE PROCESS AND SAFETY HAZARD. AS A RESULT, IT WILL EFFECT THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | LEAKAGE, WEAR | VALVE BODY, SEAT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | 0.34 | 1.88 | 335.7353 | - | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | DISCONNECT UTILITY AT THE ACTUATOR AND DROP THE VALVE FROM THE PROCESS LINE. REMOVE THE ACTUATOR AND YOKE ASSEMBLY FROM THE VALVE. CHECK THE VALVE INTERNALS AND PERFORM LAPPING OF SEAT AND PLUG. RE-ASSEMBLE THE VALVE. RE-INSTALL INTO PROCESS LINE. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 24 | MONTH(S)
SWITCH, LIMIT | TO CONTROL THE MACHINE AND ITS MOVING PARTS FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF LIMIT SWITCH CLOSE {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WOULDN'T ABLE TO GIVE EXACT POSITION OF THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT THE SWITCH FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK SWITCH CONTACTS ARE NOT PITTED OR OXIDIZED. CARRY OUT TIGHTENING OF ALL CONNECTIONS. ENSURE THAT CABLE INSULATION IS NOT DAMAGED. CHECK FOR PROPER SUPPLY VOLTAGES. PERFORM FUNCTION TEST OF LIMIT SWITCHES USING A CONTINUITY TEST FOR CORRECTNESS OF OPERATION. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
SWITCH, LIMIT | TO CONTROL THE MACHINE AND ITS MOVING PARTS FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF LIMIT SWITCH CLOSE {EQUIPMENT TAG NUMBER} WILL GIVES IMPROPER INFORMATION OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | BLOCKAGE/PLUGGED, FAULTY SIGNAL/INDICATION/ALARM, INSTRUMENT FAILURE-GENERAL, NO SIGNAL/INDICATION/ALARM | ELECTRONICS (CONDITIONING), SENSING ELEMENT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.58 | 1.47 | 3.09 | 77.6531 | 2.2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT THE SWITCH FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK SWITCH CONTACTS ARE NOT PITTED OR OXIDIZED. CARRY OUT TIGHTENING OF ALL CONNECTIONS. ENSURE THAT NO ELECTRICAL INTERFERENCE DUE TO CABLE INSULATION DAMAGE OR IMPROPER LOOP WIRING. PERFORM FUNCTION TEST OF LIMIT SWITCHES USING A CONTINUITY TEST FOR CORRECTNESS OF OPERATION. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
SWITCH, POSITION | TO CONTROL THE POSITION OF ASSOCIATED EQUIPMENT FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF POSITION SWITCH {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WOULDN'T ABLE TO GIVE EXACT POSITION OF ASSOCIATED EQUIPMENT FOR THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT THE SWITCH FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK SWITCH CONTACTS ARE NOT PITTED OR OXIDIZED. CARRY OUT TIGHTENING OF ALL CONNECTIONS. ENSURE THAT CABLE INSULATION IS NOT DAMAGED. CHECK FOR PROPER SUPPLY VOLTAGES. PERFORM FUNCTION TEST OF POSITION SWITCHES USING A CONTINUITY TEST FOR CORRECTNESS OF OPERATION. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
SWITCH, POSITION | TO CONTROL THE POSITION OF ASSOCIATED EQUIPMENT FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF POSITION SWITCH {EQUIPMENT TAG NUMBER} WILL GIVES IMPROPER INFORMATION OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | BLOCKAGE/PLUGGED, FAULTY SIGNAL/INDICATION/ALARM, INSTRUMENT FAILURE-GENERAL, NO SIGNAL/INDICATION/ALARM | ELECTRONICS (CONDITIONING), SENSING ELEMENT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.58 | 1.47 | 3.09 | 77.6531 | 2.2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT THE SWITCH FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK SWITCH CONTACTS ARE NOT PITTED OR OXIDIZED. CARRY OUT TIGHTENING OF ALL CONNECTIONS. ENSURE THAT NO ELECTRICAL INTERFERENCE DUE TO CABLE INSULATION DAMAGE OR IMPROPER LOOP WIRING. PERFORM FUNCTION TEST OF POSITION SWITCHES USING A CONTINUITY TEST FOR CORRECTNESS OF OPERATION. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
VALVE, PRESSURE CONTROL | TO CONTROL THE PRESSURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-PROCESS MEDIUM. | EXTERNAL LEAKAGE-PROCESS MEDIUM | DEGRADED | ELP | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | EXTERNAL LEAKAGE OF PRESSURE CONTROL VALVE {EQUIPMENT TAG NUMBER} CAN LEAD TO THE UNWANTED PRESSURE DROP ACROSS THE VALVE, WHICH MAY CAUSE DISTURBANCE IN OPERATION AND ENVIRONMENTAL CONSEQUENCES MAY HAPPEN. | LOOSENESS | STEM | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 2 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENT/ACTION TO MITIGATE THE LEAKAGE. CHECK FOR BOLTS TIGHTNESS. REPLACE CONSUMABLES LIKE GASKETS, O-RINGS ETC. (FOR DETAIL, REFER TO PMR) | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, PRESSURE CONTROL | TO CONTROL THE PRESSURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-UTILITY MEDIUM. | EXTERNAL LEAKAGE-UTILITY MEDIUM | DEGRADED | ELU | NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | EXTERNAL LEAKAGE-UTILITY MEDIUM OF PRESSURE CONTROL VALVE {EQUIPMENT TAG NUMBER} CAN LEAD TO THE UNWANTED PRESSURE DROP ACROSS THE VALVE, WHICH MAY CAUSE DISTURBANCE IN {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} AND ITS OPERATION AND ENVIRONMENTAL CONSEQUENCES MAY HAPPEN. | MECHANICAL FAILURE-GENERAL | SUBUNIT | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 4 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENTS/ACTION TO MITIGATE THE LEAKAGE. REPLACE CONSUMABLES LIKE GASKETS, O RINGS ETC. (FOR DETAIL, REFER TO PMR) | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, PRESSURE CONTROL | TO CONTROL THE PRESSURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF PLUGGED/CHOKED. | PLUGGED/CHOKED | DEGRADED | PLU | AGE-RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | IF PRESSURE CONTROL VALVE {EQUIPMENT TAG NUMBER} PLUGGED/CHOKED DUE TO FOREIGN MATERIAL, IT WOULD NOT WORK PROPERLY AND ULTIMATELY IT WILL LEAD TO PROCESS AT RISK. | BLOCKAGE/PLUGGED | CLOSURE MEMBER (BALL/GATE/DISC/ETC.) | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.12 | 0.76 | 1.86 | 150.1973 | - | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | PERFORM MAJOR OVERHAULING OF THE VALVE, SEAT DISC LAPPING, CLEANING AND SERVICING OF VALVE INTERNALS, AND REPLACEMENT OF ALL SEALS/SOFT GOODS. PERFORM LEAK TEST OF THE VALVE AND ENSURE THAT VALVE CONFORMS TO THE DESIGN VALVE LEAKAGE CLASSIFICATION AS SET OUT IN THE VALVE TAG PLATE OR DATASHEET. ENSURE THE CONTROL VALVE COMPONENTS AND ASSOCIATED CABLING ARE IN GOOD CONDITION, SECURELY FITTED AND FIT FOR PURPOSE. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 36 | MONTH(S)
VALVE, PRESSURE CONTROL | TO CONTROL THE PRESSURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF VALVE LEAKAGE IN CLOSED POSITION. | VALVE LEAKAGE IN CLOSED POSITION | CRITICAL | LCP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF VALVE LEAKAGE IN CLOSED POSITION OF PRESSURE CONTROL VALVE {EQUIPMENT TAG NUMBER} EXCEEDS THAN ACCEPTABLE LEAKAGE RATE, SO IT WOULD NOT BE POSSIBLE TO CONTROL THE PROCESS, WHICH RESULT AS PROCESS DISTURBANCE. | LOOSENESS, CORROSION, INSTRUMENT FAILURE-GENERAL | PACKING, SEAT RINGS, SUBUNIT | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 10 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | PERFORM MAJOR OVERHAULING OF THE VALVE, SEAT DISC LAPPING, CLEANING AND SERVICING OF VALVE INTERNALS, AND REPLACEMENT OF ALL SEALS/SOFT GOODS. PERFORM LEAK TEST OF THE VALVE AND ENSURE THAT VALVE CONFORMS TO THE DESIGN VALVE LEAKAGE CLASSIFICATION AS SET OUT IN THE VALVE TAG PLATE OR DATASHEET. ENSURE THE CONTROL VALVE COMPONENTS AND ASSOCIATED CABLING ARE IN GOOD CONDITION, SECURELY FITTED AND FIT FOR PURPOSE. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 36 | MONTH(S)
VALVE, PRESSURE CONTROL | TO CONTROL THE PRESSURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO REGULATE. | FAIL TO REGULATE | CRITICAL | FTR | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF PRESSURE CONTROL VALVE {EQUIPMENT TAG NUMBER} FAIL TO REGULATE, IT WOULD NOT BE POSSIBLE TO CONTROL/KEEP THE PROCESS AT A SET POINT, THIS MAY LEADS TO PROCESS DISTURBANCE. | BLOCKAGE/PLUGGED, INSTRUMENT FAILURE-GENERAL | VALVE BODY W/INTERNALS | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.28 | 1.14 | 2.46 | 100.1316 | 2.7 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT FOR ACTUATOR AND ALL THE TUBING CONNECTIONS FOR UTILITY LEAKAGE AND CHECK POSITIONER FEEDBACK LINK FOR LOOSENESS. ENSURE THAT PROPER INSTRUMENT AIR SUPPLY IS PROVIDING TO POSITIONER AND ACTUATOR AS PER DATA SHEET. ENSURE THAT STEM COUPLING (STEM CONNECTOR) OF ACTUATOR AND VALVE BODY IS TIGHTENED AND PROPERLY ADJUSTED. PERFORM LUBRICATION OF VALVE AND GEARBOX(IF PRESENT). CHECK VALVE TRAVEL IS SAME AS VALVE DATA PLATE. IF THE VALVE STEM TRAVEL INDICATION DIDN’T SHOW CORRECTLY 0% OR 100% TRAVEL AND ANY OFFSET FOUND, PERFORM CALIBRATION OF THE VALVE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 12 | MONTH(S)
VALVE, TEMPERATURE CONTROL | TO CONTROL THE TEMPERATURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-PROCESS MEDIUM. | EXTERNAL LEAKAGE-PROCESS MEDIUM | DEGRADED | ELP | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | EXTERNAL LEAKAGE OF TEMPERATURE CONTROL VALVE {EQUIPMENT TAG NUMBER} CAN LEAD TO THE UNWANTED TEMPERATURE ACROSS THE VALVE, WHICH MAY CAUSE DISTURBANCE IN OPERATION AND ENVIRONMENTAL CONSEQUENCES. | LOOSENESS | STEM | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 2 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENT/ACTION TO MITIGATE THE LEAKAGE. CHECK FOR BOLTS TIGHTNESS. REPLACE CONSUMABLES LIKE GASKETS, O-RINGS ETC. (FOR DETAIL, REFER TO PMR) | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, TEMPERATURE CONTROL | TO CONTROL THE TEMPERATURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-UTILITY MEDIUM. | EXTERNAL LEAKAGE-UTILITY MEDIUM | DEGRADED | ELU | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | EXTERNAL LEAKAGE-UTILITY MEDIUM FROM TEMPERATURE CONTROL VALVE {EQUIPMENT TAG NUMBER} MOUNTED ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}, CAN LEAD TO THE ABRUPT/UNWANTED CHANGE IN THE VALVE STATE AND THUS LIMITING THE VALVE TO PERFORM TASK EFFICIENTLY. | MECHANICAL FAILURE-GENERAL | SUBUNIT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 4 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENTS/ACTION TO MITIGATE THE LEAKAGE. REPLACE CONSUMABLES LIKE GASKETS, O RINGS ETC. (FOR DETAIL, REFER TO PMR) | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, TEMPERATURE CONTROL | TO CONTROL THE TEMPERATURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF PLUGGED/CHOKED. | PLUGGED/CHOKED | DEGRADED | PLU | AGE-RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | IF TEMPERATURE CONTROL VALVE {EQUIPMENT TAG NUMBER} PLUGGED/CHOKED DUE TO FOREIGN MATERIAL, IT WOULD NOT WORK PROPERLY AND ULTIMATELY IT WILL LEAD TO PROCESS AT RISK. | BLOCKAGE/PLUGGED | CLOSURE MEMBER (BALL/GATE/DISC/ETC.) | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.12 | 0.76 | 1.86 | 150.1973 | - | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | PERFORM MAJOR OVERHAULING OF THE VALVE, SEAT DISC LAPPING, CLEANING AND SERVICING OF VALVE INTERNALS, AND REPLACEMENT OF ALL SEALS/SOFT GOODS. PERFORM LEAK TEST OF THE VALVE AND ENSURE THAT VALVE CONFORMS TO THE DESIGN VALVE LEAKAGE CLASSIFICATION AS SET OUT IN THE VALVE TAG PLATE OR DATASHEET. ENSURE THE CONTROL VALVE COMPONENTS AND ASSOCIATED CABLING ARE IN GOOD CONDITION, SECURELY FITTED AND FIT FOR PURPOSE. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 36 | MONTH(S)
VALVE, TEMPERATURE CONTROL | TO CONTROL THE TEMPERATURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF VALVE LEAKAGE IN CLOSED POSITION. | VALVE LEAKAGE IN CLOSED POSITION | CRITICAL | LCP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF VALVE LEAKAGE IN CLOSED POSITION OF TEMPERATURE CONTROL VALVE {EQUIPMENT TAG NUMBER} EXCEEDS THAN ACCEPTABLE LEAKAGE RATE, SO IT WOULD NOT BE POSSIBLE TO CONTROL THE OPERATION, WHICH RESULT AS OPERATION DISTURBANCE. | LOOSENESS, CORROSION, INSTRUMENT FAILURE-GENERAL | PACKING, SEAT RINGS, SUBUNIT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 10 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | PERFORM MAJOR OVERHAULING OF THE VALVE, SEAT DISC LAPPING, CLEANING AND SERVICING OF VALVE INTERNALS, AND REPLACEMENT OF ALL SEALS/SOFT GOODS. PERFORM LEAK TEST OF THE VALVE AND ENSURE THAT VALVE CONFORMS TO THE DESIGN VALVE LEAKAGE CLASSIFICATION AS SET OUT IN THE VALVE TAG PLATE OR DATASHEET. ENSURE THE CONTROL VALVE COMPONENTS AND ASSOCIATED CABLING ARE IN GOOD CONDITION, SECURELY FITTED AND FIT FOR PURPOSE. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 36 | MONTH(S)
VALVE, TEMPERATURE CONTROL | TO CONTROL THE TEMPERATURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO REGULATE. | FAIL TO REGULATE | CRITICAL | FTR | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF TEMPERATURE CONTROL VALVE {EQUIPMENT TAG NUMBER} FAIL TO REGULATE, IT WOULD NOT BE POSSIBLE TO CONTROL/KEEP THE OPERATION AT A SET POINT, THIS MAY LEADS TO OPERATION DISTURBANCE. | BLOCKAGE/PLUGGED, INSTRUMENT FAILURE-GENERAL | VALVE BODY W/INTERNALS | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.28 | 1.14 | 2.46 | 100.1316 | 2.7 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT FOR ACTUATOR AND ALL THE TUBING CONNECTIONS FOR UTILITY LEAKAGE AND CHECK POSITIONER FEEDBACK LINK FOR LOOSENESS. ENSURE THAT PROPER INSTRUMENT AIR SUPPLY IS PROVIDING TO POSITIONER AND ACTUATOR AS PER DATA SHEET. ENSURE THAT STEM COUPLING (STEM CONNECTOR) OF ACTUATOR AND VALVE BODY IS TIGHTENED AND PROPERLY ADJUSTED. PERFORM LUBRICATION OF VALVE AND GEARBOX(IF PRESENT). CHECK VALVE TRAVEL IS SAME AS VALVE DATA PLATE. IF THE VALVE STEM TRAVEL INDICATION DIDN’T SHOW CORRECTLY 0% OR 100% TRAVEL AND ANY OFFSET FOUND, PERFORM CALIBRATION OF THE VALVE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 12 | MONTH(S)
VALVE, CHOKE | TO CONTROL/REGULATE THE FLOW AND PRESSURE FROM RESERVOIR OR THE DOWNSTREAM PRESSURE IN THE FLOWLINES OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-PROCESS MEDIUM. | EXTERNAL LEAKAGE-PROCESS MEDIUM | CRITICAL | ELP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | EXTERNAL LEAKAGE IN CHOKE VALVE {EQUIPMENT TAG NUMBER} WILL LEAD TO SAFETY HAZARD, EXCESSIVE LEAKAGE CAN CAUSE PROCESS INTERRUPTION AS WELL. | CORROSION, LEAKAGE, MECHANICAL FAILURE-GENERAL, MATERIAL FAILURE-GENERAL, LOOSENESS, | BONNET, FLANGE, PACKING, SEALS, SEAT RINGS, STEM, SUBUNIT, VALVE BODY W/INTERNALS | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | 0.36 | 1.88 | 317.0833 | 32 | 1.3 | 13.57 | 37.01 | 8.4119 | 6.3 | 497 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENTS OF GASKETS/PACKINGS/RINGS TO MITIGATE LEAKAGE OR REPLACE VALVE/INTERNALS. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, CHOKE | TO CONTROL/REGULATE THE FLOW AND PRESSURE FROM RESERVOIR OR THE DOWNSTREAM PRESSURE IN THE FLOWLINES OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO OPEN ON DEMAND. | FAIL TO OPEN ON DEMAND | CRITICAL | FTO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | IF CHOKE VALVE {EQUIPMENT TAG NUMBER} FAIL TO OPEN ON DEMAND, IT WOULD NOT BE POSSIBLE TO CONTROL/KEEP THE PROCESS AT A SET POINT, THIS MAY LEADS TO PROCESS DISTURBANCE. | BLOCKAGE/PLUGGED, MECHANICAL FAILURE-GENERAL, STICKING, INSTRUMENT FAILURE-GENERAL | VALVE BODY W/INTERNALS | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 1.08 | 3.46 | 105.4944 | 2.3 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | PERFORM LUBRICATION/GREASING. CYCLE THE VALVE FULLY OPEN AND CLOSED TO CHECK FOR FREEDOM OF OPERATION. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 720 | DAY(S)
VALVE, CHOKE | TO CONTROL/REGULATE THE FLOW AND PRESSURE FROM RESERVOIR OR THE DOWNSTREAM PRESSURE IN THE FLOWLINES OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF STRUCTURAL DEFICIENCY. | STRUCTURAL DEFICIENCY | CRITICAL | STD | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | STRUCTURAL DEFICIENCY OF CHOKE VALVE {EQUIPMENT TAG NUMBER} WILL CAUSE DEGRADED OPERATION OF VALVE WHICH MAY RESULT IN LEAKAGE IN CLOSED POSITION. THIS MAY ALSO EFFECT THE ISOLATION AS CHOKE VALVE WILL NOT ACT PROPERLY DURING SURFACE DISASTER. IT MAY CAUSE THE SAFETY AND ENVIRONMENTAL EFFECTS IN CASE OF EXTERNAL LEAKAGE. | BREAKAGE, CORROSION, INSTRUMENT FAILURE-GENERAL, MATERIAL FAILURE-GENERAL, MISC. EXTERNAL INFLUENCES | BONNET, CABLING & JUNCTION BOXES, CLOSURE MEMBER (BALL/GATE/DISC), PILOT VALVE, VALVE BODY W/INTRNALS | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | 0.17 | 0.93 | 471.4706 | 5 | 1.3 | 13.57 | 37.01 | 8.4119 | 6.3 | 497 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | SHOP INSPECTION/OVERHAULING: PERFORM OVERHAULING OF THE VALVE AT WORKSHOP. A BENCH TEST SHALL BE PERFORMED, HOWEVER, THE VALVE SHALL BE CLEANED OR STEAMED OUT PRIOR TO THE BENCH TEST. ADDITIONALLY, A VISUAL INSPECTION SHALL BE PERFORMED WHERE DETAILED DOCUMENTATION OF THE CONDITION OF THE VALVE INTERNAL COMPONENTS SHALL BE MADE. VISUAL INSPECTION OF DIFFERENT PARTS OF SAFETY VALVE SHALL BE DONE AFTER DISMANTLING TO CHECK THE FOLLOWING: I) CONDITION OF FLANGES FOR PITTING, ROUGHENING, DECREASE IN WIDTH OF SEATING SURFACE ETC. II) SPRING, FOR EVIDENCE OF BENDING, CORROSION OR CRACKING, FREE LENGTH OF SPRING. III) POSITION OF SET SCREWS AND OPENING IN BONNET. IV) INLET/OUTLET NOZZLES FOR EVIDENCE OF DEPOSITS FOREIGN MATERIAL AND CORROSION. V) CONDITION OF EXTERNAL SURFACE AND EVIDENCE OF MECHANICAL DAMAGE. VI) CONDITIONS OF STEM, GUIDE DISC, NOZZLES ETC. FOR EVIDENCE OF WEAR AND CORROSION. VII) SEATING SURFACE OF DISC AND NOZZLE SHALL BE CRITICALLY EXAMINED FOR ROUGHNESS OR DAMAGE WHICH COULD RESULT IN VALVE LEAKAGE AND MAY NEED CORRECTION. CARE MUST BE TAKEN TO ENSURE FLATNESS OF SEATS. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 720 | DAY(S)
I/P CONVERTER | TO CONVERT AN ELECTRICAL SIGNAL INTO A PNEUMATIC SIGNAL WITH THE HELP OF VALVE ACTUATOR FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF I/P CONVERTER {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WOULD NOT BE ABLE TO MANIPULATE THE DESIRED SIGNAL TO {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | LOOP CABLE DAMAGE, MECHANISM FAULTY, AIR PRESSURE NOT AVAILABLE, ZERO/SPAN ADJUSTMENT PROBLEM | I/P CONVERTOR | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | PERFORM FUNCTION TEST OF I/P CONVERTER. IF ANY OFFSET FOUND. MONITOR I/P CONVERTER FUNCTIONALITY AND PERFORM CALIBRATION. PERFORM CALIBRATION OF THE I/P CONVERTER WITH A SIMULATED SIGNAL FROM 4 ~ 20 MA AND ADJUST CORRESPONDING 3 ~ 15 PSI SIGNAL. IF GENERAL CONDITION OF I/P CONVERTER OR I/P CONVERTER IS NOT FUNCTIONING SATISFACTORILY, CARRY OUT SERVICING IN ACCORDANCE WITH RELEVANT PROCEDURES AND FUNCTION TEST I/P CONVERTER ON COMPLETION. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 18 | MONTH(S)
I/P CONVERTER | TO CONVERT AN ELECTRICAL SIGNAL INTO A PNEUMATIC SIGNAL WITH THE HELP OF VALVE ACTUATOR FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF ERRATIC OUTPUT. | ERRATIC OUTPUT | DEGRADED | ERO | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | ERRATIC OUTPUT OF I/P CONVERTER {EQUIPMENT TAG NUMBER} WILL DIRECTLY EFFECT TO THE SWITCHING OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. WHICH WILL LEAD TO THE PARTIAL FAILURE OF ASSOCIATED EQUIPMENT. | LOOP CABLE DAMAGE, MECHANISM FAULTY, GAIN TOO HIGH OR TOO LOW, PERMANENT MAGNET WEEKENED, ERRATIC INPUT SIGNAL | I/P CONVERTOR | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | PERFORM FUNCTION TEST OF I/P CONVERTER. IF ANY OFFSET FOUND. MONITOR I/P CONVERTER FUNCTIONALITY AND PERFORM CALIBRATION. PERFORM CALIBRATION OF THE I/P CONVERTER WITH A SIMULATED SIGNAL FROM 4 ~ 20 MA AND ADJUST CORRESPONDING 3 ~ 15 PSI SIGNAL. IF GENERAL CONDITION OF I/P CONVERTER OR I/P CONVERTER IS NOT FUNCTIONING SATISFACTORILY, CARRY OUT SERVICING IN ACCORDANCE WITH RELEVANT PROCEDURES AND FUNCTION TEST I/P CONVERTER ON COMPLETION. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 18 | MONTH(S)
I/P CONVERTER | TO CONVERT AN ELECTRICAL SIGNAL INTO A PNEUMATIC SIGNAL WITH THE HELP OF VALVE ACTUATOR FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | THE I/P CONVERTER {EQUIPMENT TAG NUMBER} CONVERT THE FALSE DESIRED OUTPUT SIGNAL FROM THE INPUT SIGNAL AND CAUSE UNSTABLE OPERATION OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | SERVER FAILURE, CONFIGURATION FAILURE, HARDWARE FAILURE | I/P CONVERTOR | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | PERFORM FUNCTION TEST OF I/P CONVERTER. IF ANY OFFSET FOUND. MONITOR I/P CONVERTER FUNCTIONALITY AND PERFORM CALIBRATION. PERFORM CALIBRATION OF THE I/P CONVERTER WITH A SIMULATED SIGNAL FROM 4 ~ 20 MA AND ADJUST CORRESPONDING 3 ~ 15 PSI SIGNAL. IF GENERAL CONDITION OF I/P CONVERTER OR I/P CONVERTER IS NOT FUNCTIONING SATISFACTORILY, CARRY OUT SERVICING IN ACCORDANCE WITH RELEVANT PROCEDURES AND FUNCTION TEST I/P CONVERTER ON COMPLETION. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 18 | MONTH(S)
DETECTOR, FLAME | TO DETECT FIRE FLAME AND TO PROVIDE EARLY WARNING OF FIRE FOR THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF ERRATIC OUTPUT. | ERRATIC OUTPUT | DEGRADED | ERO | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IN CASE OF ERRATIC OUTPUT OF FLAME DETECTOR {EQUIPMENT TAG NUMBER} MAY CAUSE UNNECESSARY ALARM OF FIRE AND GAS, WHICH MAY CAUSE DISTRUBANCE IN ROUTINES WORKS. | CLEARANCE/ALIGNMENT FAILURE, CONTAMINATION, FAULTY SIGNAL/INDICATION/ALARM, MATERIAL FAILURE-GENERAL, OUT OF ADJUSTMENT, VIBRATION | DETECTOR HEAD, SUBUNIT | 5 | E | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | 0.01 | 1.64 | 5.9 | 69.6037 | 2.6 | 1.7 | 9.74 | 23.21 | 11.7197 | 1.8 | 429 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | FUNCTION TEST AND CALIBRATION | VISUALLY INSPECT THE DEVICE FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. INSPECT AND CLEAN THE DETECTOR DISPLAY, JUNCTION BOX AND CABLE GLAND. CHECK FOR ANY PHYSICAL DAMAGE. CHECK ALARMS AND OTHER SETTINGS. CARRY OUT FUNCTION TEST AND CALIBRATION AS PER PROCEDURE. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 6 | MONTH(S)
DETECTOR, FLAME | TO DETECT FIRE FLAME AND TO PROVIDE EARLY WARNING OF FIRE FOR THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF FLAME DETECTOR {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, THERE WILL NOT BE ANY DETECTION OF PRESENCE OF FLAME RESULTING IN INJURY TO PERSONNEL WORKING NEARBY, BUSINESS LOSS AND EQUIPMENT DAMAGE. | CONTAMINATION, EXTERNAL INFLUENCE-GENERAL, INSTRUMENT FAILURE-GENERAL, OUT OF ADJUSTMENT, SHORT CIRCUITING, VIBRATION | DETECTOR HEAD, SUBUNIT | 4 | C | RISK RANK 2 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | - | 0.18 | 0.93 | 434.1444 | 3.8 | 1.7 | 9.74 | 23.21 | 11.7197 | 1.8 | 429 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | FUNCTION TEST AND CALIBRATION | DETAIL CHECK AND INSPECT FLAME DETECTOR AND WIRING PHYSICAL CONDITION. TIGHTEN ALL TERMINALS. CHECK FUSES AND POWER SUPPLY. CARRY OUT FUNCTION TEST FOR THE DETECTOR AS PER PROCEDURE. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 6 | MONTH(S)
DETECTOR, FLAME | TO DETECT FIRE FLAME AND TO PROVIDE EARLY WARNING OF FIRE FOR THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | DEGRADED | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS OF FLAME DETECTOR {EQUIPMENT TAG NUMBER} MAY CAUSE DELAY IN ALARM. | CLEARANCE/ALIGNMENT FAILURE, COMMON MODE FAILURE, CONTAMINATION, INSTRUMENT FAILURE-GENERAL, OUT OF ADJUSTMENT | CABLING, DETECTOR HEAD, CABINET, SUBUNIT | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | 0.0002 | 0.12 | 0.47 | 951.25 | 2.5 | 1.7 | 9.74 | 23.21 | 11.7197 | 1.8 | 429 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | FUNCTION TEST AND CALIBRATION | DETAIL CHECK AND INSPECT FLAME DETECTOR AND WIRING PHYSICAL CONDITION. CHECK FOR ANY PHYSICAL DAMAGE. CARRY OUT FUNCTION TEST FOR THE DETECTOR WITH A FIRE SIMULATOR AS PER PROCEDURE. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 6 | MONTH(S)
DETECTOR, HEAT | TO DETECT HEAT OR TO RESPOND WHEN THE CONVICTED THERMAL ENERGY OF A FIRE INCREASES THE TEMPERATURE OF A HEAT SENSITIVE ELEMENT FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF HEAT DETECTOR {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, THERE WILL NOT BE ANY DETECTION OF HEAT RESULTING IN INJURY TO PERSONNEL WORKING NEARBY. | CONTAMINATION, EXTERNAL INFLUENCE-GENERAL, INSTRUMENT FAILURE-GENERAL, OUT OF ADJUSTMENT, SHORT CIRCUITING, VIBRATION | DETECTOR HEAD, SUBUNIT | 4 | C | RISK RANK 2 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | - | 0.18 | 0.93 | 434.1444 | 3.8 | 1.7 | 9.74 | 23.21 | 11.7197 | 1.8 | 429 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CLEAN WEATHER PROTECTION HOUSING, DUST BARRIER AND OPTICAL SURFACE. CHECK ANY PHYSICAL DAMAGE FOR THE HEAT DETECTOR. CHECK VOLTAGES AND CABLE INSULATION. ENSURE THAT OUTPUT RELAY IS FUNCTIONING PROPERLY. PERFORM FUNCTION TEST AS PER PROCEDURE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 1 | YEAR(S)
DETECTOR, HEAT | TO DETECT HEAT OR TO RESPOND WHEN THE CONVICTED THERMAL ENERGY OF A FIRE INCREASES THE TEMPERATURE OF A HEAT SENSITIVE ELEMENT FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | DEGRADED | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS OF HEAT DETECTOR {EQUIPMENT TAG NUMBER} MAY CAUSE DELAY IN ALARM. | CLEARANCE/ALIGNMENT FAILURE, COMMON MODE FAILURE, CONTAMINATION, INSTRUMENT FAILURE-GENERAL, OUT OF ADJUSTMENT | CABLING, DETECTOR HEAD, CABINET, SUBUNIT | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | 0.0002 | 0.12 | 0.47 | 951.25 | 2.5 | 1.7 | 9.74 | 23.21 | 11.7197 | 1.8 | 429 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CHECK/INSPECT DETECTOR CONDITION FOR ANY DAMAGE. TIGHTEN ALL TERMINALS AND INSPECT LOOP WIRING. CARRY OUT FUNCTION TEST FOR THE DETECTOR AS PER PROCEDURE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 1 | YEAR(S)
DETECTOR, HEAT | TO DETECT HEAT OR TO RESPOND WHEN THE CONVICTED THERMAL ENERGY OF A FIRE INCREASES THE TEMPERATURE OF A HEAT SENSITIVE ELEMENT FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF HEAT DETECTOR {EQUIPMENT TAG NUMBER} WILL INDICATE WRONG INFORMATION ABOUT PRESENCE OF FLAME CAUSING MAJOR INJURY DUE TO FIRE IF HYDROCARBON IS PRESENT IN WORK SPACE. | CONTAMINATION, EXTERNAL INFLUENCE-GENERAL, INSTRUMENT FAILURE-GENERAL, LOOSENESS, MISC. EXTERNAL INFLUENCES, MISCELLANEOUS-GENERAL, OUT OF ADJUSTMENT | DETECTOR HEAD, SUBUNIT | 4 | C | RISK RANK 2 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | - | 0.26 | 1.44 | 439.0384 | 2.7 | 1.7 | 9.74 | 23.21 | 11.7197 | 1.8 | 429 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | INSPECT AND CHECK THAT DETECTOR IS IN GOOD CONDITION AND FREE FROM OBSTRUCTIONS OR DUST ON THE WINDOW. CHECK FOR LOOSENESS OF THE HOUSING COVER AND TERMINAL BOX OF DETECTOR. INSPECT WIRING FOR CRACKED, BROKEN, OR DETERIORATED INSULATION AND EXPOSED CONDUCTOR. PERFORM FUNCTION TEST AS PER PROCEDURE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 1 | YEAR(S)
DETECTOR, GAS | TO DETECT HYDROCARBON GASES FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF ERRATIC OUTPUT. | ERRATIC OUTPUT | DEGRADED | ERO | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IN CASE OF ERRATIC OUTPUT OF GAS DETECTOR {EQUIPMENT TAG NUMBER} MAY CAUSE UNNECESSARY ALARM OF F&G, WHICH MAY CAUSE DISTRUBANCE IN ROUTINES WORKS. | CLEARANCE/ALIGNMENT FAILURE, CONTAMINATION, FAULTY SIGNAL/INDICATION/ALARM, MATERIAL FAILURE-GENERAL, OUT OF ADJUSTMENT, VIBRATION | DETECTOR HEAD, SUBUNIT | 5 | E | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | 0.01 | 1.64 | 5.9 | 69.6037 | 2.6 | 1.7 | 9.74 | 23.21 | 11.7197 | 1.8 | 429 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | FUNCTION TEST AND CALIBRATION | VISUALLY INSPECT THE DEVICE FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. INSPECT AND CLEAN THE DETECTOR DISPLAY, JUNCTION BOX AND CABLE GLAND. CHECK FOR ANY PHYSICAL DAMAGE. CHECK ALARMS AND OTHER SETTINGS. CARRY OUT FUNCTION TEST AND CALIBRATION AS PER PROCEDURE. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
DETECTOR, GAS | TO DETECT HYDROCARBON GASES FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF GAS DETECTOR {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, THERE WILL NOT BE ANY DETECTION OF GAS RESULTING IN INJURY TO PERSONNEL WORKING NEARBY. | CONTAMINATION, EXTERNAL INFLUENCE-GENERAL, INSTRUMENT FAILURE-GENERAL, OUT OF ADJUSTMENT, SHORT CIRCUITING, VIBRATION | DETECTOR HEAD, SUBUNIT | 4 | C | RISK RANK 2 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | - | 0.18 | 0.93 | 434.1444 | 3.8 | 1.7 | 9.74 | 23.21 | 11.7197 | 1.8 | 429 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | FUNCTION TEST AND CALIBRATION | DETAIL CHECK AND INSPECT GAS DETECTOR AND WIRING PHYSICAL CONDITION. TIGHTEN ALL TERMINALS. CHECK FUSES AND POWER SUPPLY. CARRY OUT FUNCTION TEST FOR THE DETECTOR AS PER PROCEDURE. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
DETECTOR, GAS | TO DETECT HYDROCARBON GASES FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | DEGRADED | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS OF GAS DETECTOR {EQUIPMENT TAG NUMBER} MAY CAUSE DELAY IN ALARM, IT HAS NO DIRECT IMAPCT ON SAFETY AND BUSINESS. | CLEARANCE/ALIGNMENT FAILURE, COMMON MODE FAILURE, CONTAMINATION, INSTRUMENT FAILURE-GENERAL, OUT OF ADJUSTMENT | CABLING, DETECTOR HEAD, CABINET, SUBUNIT | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | 0.0002 | 0.12 | 0.47 | 951.25 | 2.5 | 1.7 | 9.74 | 23.21 | 11.7197 | 1.8 | 429 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | FUNCTION TEST AND CALIBRATION | DETAIL CHECK AND INSPECT GAS DETECTOR AND WIRING PHYSICAL CONDITION. CHECK FOR ANY PHYSICAL DAMAGE. CARRY OUT FUNCTION TEST FOR THE DETECTOR WITH A FIRE SIMULATOR AS PER PROCEDURE. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
THERMOWELL | TO DETECT PROCESS TEMPERATURE WITHOUT OPENING A HOLE IN THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF BENDING-FATIGUE. | BENDING-FATIGUE | DEGRADED | BNF | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | BENDING-FATIGUE OF THERMOWELL {EQUIPMENT TAG NUMBER} MAY CAUSE ERROR IN MEASUREMENT. | MATERIAL FAILURE-GENERAL | THERMOWELL | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | VISUALLY INSPECT FOR ANY CORROSION, BENDING AND DEFORMATIONS. CHECK AND INSPECT THE THERMOWELL FOR ANY DAMAGES. TAKE CORRECTIVE TASK AND REPLACE UPON FAILURE. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 3 | YEAR(S)
THERMOWELL | TO DETECT PROCESS TEMPERATURE WITHOUT OPENING A HOLE IN THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-PROCESS MEDIUM. | EXTERNAL LEAKAGE-PROCESS MEDIUM | DEGRADED | ELP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | EXTERNAL LEAKAGE FROM THERMOWELL {EQUIPMENT TAG NUMBER} MAY IMPACT THE WORKING OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | MATERIAL FAILURE-GENERAL | THERMOWELL | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | CHECK AND INSPECT THE THERMOWELL FOR ANY DAMAGES. INSPECT FOR PROCESS LEAKAGES. TAKE CORRECTIVE TASK AND REPLACE UPON FAILURE. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 3 | YEAR(S)
DETECTOR, SMOKE | TO DETECT SMOKE AND RESPONSE FOR FIRE ZONE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF ERRATIC OUTPUT. | ERRATIC OUTPUT | DEGRADED | ERO | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IN CASE OF ERRATIC OUTPUT OF SMOKE DETECTOR {EQUIPMENT TAG NUMBER} MAY CAUSE UNNECESSARY ALARM OF FIRE AND GAS, WHICH MAY CAUSE DISTRUBANCE IN ROUTINES WORKS. | CLEARANCE/ALIGNMENT FAILURE, CONTAMINATION, FAULTY SIGNAL/INDICATION/ALARM, MATERIAL FAILURE-GENERAL, OUT OF ADJUSTMENT, VIBRATION | DETECTOR HEAD, SUBUNIT | 5 | E | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | 0.01 | 1.64 | 5.9 | 69.6037 | 2.6 | 1.7 | 9.74 | 23.21 | 11.7197 | 1.8 | 429 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | FUNCTION TEST AND CALIBRATION | VISUALLY INSPECT THE DEVICE FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. INSPECT AND CLEAN THE DETECTOR DISPLAY, JUNCTION BOX AND CABLE GLAND. CHECK FOR ANY PHYSICAL DAMAGE. CHECK ALARMS AND OTHER SETTINGS. CARRY OUT FUNCTION TEST AND CALIBRATION AS PER PROCEDURE. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
DETECTOR, SMOKE | TO DETECT SMOKE AND RESPONSE FOR FIRE ZONE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF SMOKE DETECTOR {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, THERE WILL NOT BE ANY DETECTION OF PRESENCE OF SMOKE RESULTING IN INJURY TO PERSONNEL WORKING NEARBY, BUSINESS LOSS AND EQUIPMENT DAMAGE. | CONTAMINATION, EXTERNAL INFLUENCE-GENERAL, INSTRUMENT FAILURE-GENERAL, OUT OF ADJUSTMENT, SHORT CIRCUITING, VIBRATION | DETECTOR HEAD, SUBUNIT | 4 | C | RISK RANK 2 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | - | 0.18 | 0.93 | 434.1444 | 3.8 | 1.7 | 9.74 | 23.21 | 11.7197 | 1.8 | 429 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | FUNCTION TEST AND CALIBRATION | DETAIL CHECK AND INSPECT SMOKE DETECTOR AND WIRING PHYSICAL CONDITION. TIGHTEN ALL TERMINALS. CHECK FUSES AND POWER SUPPLY. CARRY OUT FUNCTION TEST FOR THE DETECTOR AS PER PROCEDURE. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
DETECTOR, SMOKE | TO DETECT SMOKE AND RESPONSE FOR FIRE ZONE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | DEGRADED | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS OF SMOKE DETECTOR {EQUIPMENT TAG NUMBER} MAY CAUSE DELAY IN ALARM. | CLEARANCE/ALIGNMENT FAILURE, COMMON MODE FAILURE, CONTAMINATION, INSTRUMENT FAILURE-GENERAL, OUT OF ADJUSTMENT | CABLING, DETECTOR HEAD, CABINET, SUBUNIT | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | 0.0002 | 0.12 | 0.47 | 951.25 | 2.5 | 1.7 | 9.74 | 23.21 | 11.7197 | 1.8 | 429 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | FUNCTION TEST AND CALIBRATION | DETAIL CHECK AND INSPECT SMOKE DETECTOR AND WIRING PHYSICAL CONDITION. CHECK FOR ANY PHYSICAL DAMAGE. CARRY OUT FUNCTION TEST FOR THE DETECTOR WITH A FIRE SIMULATOR AS PER PROCEDURE. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
ELEMENT, POSITION | TO DETECT THE POSITION OF {SERVICE} AND GIVE INFORMATION FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF ABNORMAL OUTPUT-LOW. | ABNORMAL OUTPUT-LOW | CRITICAL | AOL | AGE-RELATED | EVIDENT | PROCESS AND OPERATIONAL | ABNORMAL OUTPUT-LOW OF POSITION ELEMENT {EQUIPMENT TAG NUMBER} ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL PROVIDE IMPROPER INFORMATION OF VALVE STATUS WHICH MAY EFFECT THE VALVE PERFORMANCE THAT MAY LEAD TO SAFETY RISK. | OUT OF ADJUSTMENT | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.29 | 1.4 | 393.4205 | 4 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND CALIBRATION | VISUALLY INSPECT THE ELEMENT FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ANY WATER INGRESS INSIDE THE HOUSING. INSPECT FOR INTERMITTENT SHORTS. CHECK FOR ADEQUATE VOLTAGE TO THE ELEMENT. CARRY OUT CALIBRATION OF ELEMENT ALONG WITH TRANSMITTER. | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 2 | YEAR(S)
ELEMENT, POSITION | TO DETECT THE POSITION OF {SERVICE} AND GIVE INFORMATION FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS OF POSITION ELEMENT {EQUIPMENT TAG NUMBER} ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL PROVIDE IMPROPER INFORMATION OF VALVE STATUS WHICH MAY EFFECT THE VALVE PERFORMANCE THAT MAY LEAD TO SAFETY RISK. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | INSPECTION, CALIBRATION AND FUNCTIONAL TEST | VISUALLY INSPECT THE ELEMENT FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ANY WATER INGRESS INSIDE THE HOUSING. INSPECT FOR INTERMITTENT SHORTS. CHECK FOR ADEQUATE VOLTAGE TO THE ELEMENT. CARRY OUT CALIBRATION OF ELEMENT ALONG WITH TRANSMITTER. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 2 | YEAR(S)
ELEMENT, POSITION | TO DETECT THE POSITION OF {SERVICE} AND GIVE INFORMATION FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE WILL OCCURE IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF POSITION ELEMENT {EQUIPMENT TAG NUMBER} ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL PROVIDE IMPROPER INFORMATION OF VALVE STATUS WHICH MAY EFFECT THE VALVE PERFORMANCE THAT MAY LEAD TO SAFETY RISK. | BLOCKAGE/PLUGGED, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM, INSTRUMENT FAILURE GENERAL | ELECTRONICS (CONDITIONING), SENSING ELEMENT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.58 | 1.47 | 3.09 | 77.6531 | 2.2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND CALIBRATION | VISUALLY INSPECT THE ELEMENT FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ANY WATER INGRESS INSIDE THE HOUSING. INSPECT FOR INTERMITTENT SHORTS. CHECK FOR ADEQUATE VOLTAGE TO THE ELEMENT. CARRY OUT CALIBRATION OF ELEMENT ALONG WITH TRANSMITTER. | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 2 | YEAR(S)
SWITCH, LEVEL | TO DETERMINE WHETHER A MATERIAL/FLUID REACHES A CERTAIN VALUE, AND ONCE IT REACHES THAT VALUE, A SIGNAL CAN BE SENT FROM THE LEVEL SWITCH TO ANOTHER DEVICE FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE WILL HAPPEN IN CASE OF ABNORMAL OUTPUT-LOW. | ABNORMAL OUTPUT-LOW | CRITICAL | AOL | AGE-RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | ABNORMAL OUTPUT-LOW OF LEVEL SWITCH {EQUIPMENT TAG NUMBER} MAY GIVE FALSE INFORMATION TO ITS CONTROLLER WHICH MAY CAUSE PROCESS DISTURBANCE. | OUT OF ADJUSTMENT | SENSING ELEMENT | 5 | E | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.06 | 1.27 | 6.02 | 89.8819 | 4 | 3.32 | 7.61 | 15.02 | 15 | 2.3 | 463 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CHECK FOR ANY DUST, MOISTURE INSIDE TERMINAL HOUSING. PERFORM TERMINAL TIGHTENING. WITH SWITCH HOUSING ASSEMBLY REMOVED, INSPECT ATTRACTING SLEEVE. READJUST PIVOT SOCKETS IF BINDING IN SWITCHING MECHANISM EXISTS. PERFORM FUNCTION TEST OF SWITCH. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
SWITCH, LEVEL | TO DETERMINE WHETHER A MATERIAL/FLUID REACHES A CERTAIN VALUE, AND ONCE IT REACHES THAT VALUE, A SIGNAL CAN BE SENT FROM THE LEVEL SWITCH TO ANOTHER DEVICE FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF LEVEL SWITCH {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WILL NOT GIVE FEEDBACK IF LEVEL REACHED TO THE SET LIMIT THAT WILL BE A RISK TO THE PROCESS. | BLOCKAGE/PLUGGED | SENSING ELEMENT | 5 | E | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.06 | 1.27 | 6.02 | 89.8819 | 2 | 3.32 | 7.61 | 15.02 | 15 | 2.3 | 463 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CHECK FOR SUPPLY VOLTAGES. CHECK FOR ANY DUST, MOISTURE INSIDE TERMINAL HOUSING. CHECK FOR PROPER LOOP WIRING AND PERFORM TERMINAL TIGHTENING. WITH SWITCH HOUSING ASSEMBLY REMOVED, INSPECT ATTRACTING SLEEVE. READJUST PIVOT SOCKETS IF BINDING IN SWITCHING MECHANISM EXISTS. PERFORM FUNCTION TEST OF SWITCH. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
SWITCH, LEVEL | TO DETERMINE WHETHER A MATERIAL/FLUID REACHES A CERTAIN VALUE, AND ONCE IT REACHES THAT VALUE, A SIGNAL CAN BE SENT FROM THE LEVEL SWITCH TO ANOTHER DEVICE FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS IN LEVEL SWITCH {EQUIPMENT TAG NUMBER} WILL NOT GIVE INDICATION WHEN LEVEL IN {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} REACHED THE SET POINT ULTIMATELY RESULTING IN PROCESS DISTURBANCE. | FAULTY SIGNAL/INDICATION/ALARM | SENSING ELEMENT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.06 | 1.27 | 6.02 | 89.8819 | 3 | 3.32 | 7.61 | 15.02 | 15 | 2.3 | 463 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | INSPECT THE SWITCH FOR ANY DEGRADATION AND ABNORMALITY. TIGHTEN TERMINAL SCREWS AND CLEAN ACCORDINGLY. CHECK FOR ANY DUST, MOISTURE INSIDE TERMINAL HOUSING. WITH SWITCH HOUSING ASSEMBLY REMOVED, INSPECT ATTRACTING SLEEVE. READJUST PIVOT SOCKETS IF BINDING IN SWITCHING MECHANISM EXISTS. PERFORM FUNCTION TEST OF SWITCH. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
SWITCH, LEVEL | TO DETERMINE WHETHER A MATERIAL/FLUID REACHES A CERTAIN VALUE, AND ONCE IT REACHES THAT VALUE, A SIGNAL CAN BE SENT FROM THE LEVEL SWITCH TO ANOTHER DEVICE FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF LEVEL SWITCH {EQUIPMENT TAG NUMBER} MAY GIVE FALSE FEEDBACK TO CONTROL SYSTEM AND CAN CAUSE PROCESS DISTURBANCE. | BLOCKAGE/PLUGGED, NO SIGNAL/INDICATION/ALARM | SENSING ELEMENT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.45 | 2.54 | 7.99 | 44.9409 | 1.5 | 3.32 | 7.61 | 15.02 | 15 | 2.3 | 463 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CHECK FOR SUPPLY VOLTAGES. CHECK FOR ANY DUST, MOISTURE INSIDE TERMINAL HOUSING. CHECK FOR LOOSE WIRING CONNECTIONS. PERFORM FUNCTION TEST OF SWITCH. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
VALVE, SUBSURFACE SAFETY | TO ENSURE SAFE OPENING/SHUTDOWN OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO CLOSE ON DEMAND. | FAIL TO CLOSE ON DEMAND | CRITICAL | FTC | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF SUBSEA SAFETY VALVE {EQUIPMENT TAG NUMBER} FAIL TO CLOSE ON DEMAND, IT WOULD AFFECT THE WELL HEAD INTEGRITY AS THE FLUID ISOLATION BY SSSV WOULD NOT BE POSSIBLE AND WELLHEAD FLUID WILL TRAVEL TOWARDS SURFACE RESULTING IN SECONDARY WELL BARRIERS TO BE ACTIVATED. THIS MAY RESULT IN HIGHER DOWNTIME AND ULTIMATELY PRODUCTION INTERRUPTION OF CONNECTED WELLHEAD. | BLOCKAGE/PLUGGED, STICKING, INSTRUMENT FAILURE-GENERAL, MECHANICAL FAILURE-GENERAL, MISCELLANEOUS-GENERAL | VALVE BODY W/INTERNALS, STEM, SUBUNIT, SPRING | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | - | 0.97 | 5.01 | 117.4804 | 3.8 | 1.3 | 13.57 | 37.01 | 8.4119 | 6.3 | 497 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | ENSURE THE VALVE BODY AND HYDRAULIC ACTUATOR IS IN GOOD CONDITION AND SECURELY FITTED. VISUALLY CHECK FOR ALL THE TUBING CONNECTIONS FOR LOOSENESS AND LEAKAGE. PERFORM FUNCTION TEST OF THE VALVE. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 180 | DAY(S)
VALVE, SUBSURFACE SAFETY | TO ENSURE SAFE OPENING/SHUTDOWN OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO OPEN ON DEMAND. | FAIL TO OPEN ON DEMAND | CRITICAL | FTO | AGE/NON-AGE RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | IF SUBSEA SAFETY VALVE {EQUIPMENT TAG NUMBER} FAIL TO OPEN ON DEMAND, WELL FLUID MIXED OR MULTIPHASE WILL NOT FLOW IN LINE WHICH WILL RESULT IN PROCESS INTERRUPTION AND PRODUCTION INTERRUPTION OF CONNECTED WELLHEAD. | BLOCKAGE/PLUGGED, CONTROL FAILURE, CORROSION, DEFORMATION, WEAR, STICKING, INSTRUMENT FAILURE-GENERAL, MECHANICAL FAILURE-GENERAL | VALVE COMPONENTS, SUBUNIT | 4 | C | RISK RANK 2 | 4 | D | RISK RANK 3 | 4 | C | RISK RANK 2 | 4 | E | RISK RANK 3 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | 0.0002 | 0.93 | 4.17 | 122.7419 | 5.9 | 1.3 | 13.57 | 37.01 | 8.4119 | 6.3 | 497 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | ENSURE THE VALVE BODY AND HYDRAULIC ACTUATOR IS IN GOOD CONDITION AND SECURELY FITTED. VISUALLY CHECK FOR ALL THE TUBING CONNECTIONS FOR LOOSENESS AND LEAKAGE. PERFORM FUNCTION TEST OF THE VALVE. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 180 | DAY(S)
VALVE, SUBSURFACE SAFETY | TO ENSURE SAFE OPENING/SHUTDOWN OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF VALVE LEAKAGE IN CLOSED POSITION. | VALVE LEAKAGE IN CLOSED POSITION | CRITICAL | LCP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | LEAKAGE WITHIN SUBSEA SAFETY VALVE {EQUIPMENT TAG NUMBER} IN CLOSE POSITION MAY CAUSE DISTURBANCE FOR X-MAS TREE MAINTENANCE OF CONNECTED WELLHEAD. THIS MAY ALSO EFFECT THE ISOLATION AS SSSV WILL NOT ACT PROPERLY DURING SURFACE DISASTER. IT MAY CAUSE THE SAFETY AND ENVIRONMENTAL EFFECTS IN CASE OF LEAKAGE OUT OF WELLHEAD. | LOOSENESS, CLEARANCE/ALIGNMENT FAILURE, CORROSION, LEAKAGE, WEAR, INSTRUMENT FAILURE-GENERAL, MATERIAL FAILURE-GENERAL, MECHANICAL FAILURE-GENERAL | VALVE BODY W/INTERNALS, VALVE COMPONENTS, SUBUNIT, SEAT RINGS, PACKING | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | 0.0003 | 0.14 | 0.55 | 815.3571 | 10 | 1.3 | 13.57 | 37.01 | 8.4119 | 6.3 | 497 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | PERFORM FUNCTION TEST OF THE VALVE AND CHECK FOR LEAKAGE. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 180 | DAY(S)
VALVE, SUBSURFACE SAFETY | TO ENSURE SAFE OPENING/SHUTDOWN OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF STRUCTURAL DEFICIENCY. | STRUCTURAL DEFICIENCY | CRITICAL | STD | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | STRUCTURAL DEFICIENCY OF SUBSEA SAFETY VALVE {EQUIPMENT TAG NUMBER} WILL CAUSE DEGRADED OPERATION OF VALVE WHICH MAY RESULT IN LEAKAGE IN CLOSED POSITION. THIS MAY ALSO EFFECT THE ISOLATION AS SUBSEA SAFETY VALVE WILL NOT ACT PROPERLY DURING SURFACE DISASTER. IT MAY CAUSE THE SAFETY AND ENVIRONMENTAL EFFECTS IN CASE OF EXTERNAL LEAKAGE. | BREAKAGE, CORROSION, INSTRUMENT FAILURE-GENERAL, MATERIAL FAILURE-GENERAL, MISC. EXTERNAL INFLUENCES | BONNET, CABLING & JUNCTION BOXES, CLOSURE MEMBER (BALL/GATE/DISC), PILOT VALVE, VALVE BODY W/INTRNALS | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | - | 0.17 | 0.93 | 471.4706 | 5 | 1.3 | 13.57 | 37.01 | 8.4119 | 6.3 | 497 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | ENSURE THE VALVE BODY AND HYDRAULIC ACTUATOR IS IN GOOD CONDITION AND SECURELY FITTED. VISUALLY CHECK FOR ALL THE TUBING CONNECTIONS FOR LOOSENESS AND LEAKAGE. PERFORM FUNCTION TEST OF THE VALVE. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 180 | DAY(S)
HORN, AUDIBLE | TO GIVE VISUAL OR SOUND INDICATION FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} IN CASE OF EMERGENCY. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF AUDIBLE HORN {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WILL NOT GIVE VISUAL OR SOUND INDICATION FOR FIRE OR EMERGENCY, WHICH IS A SAFETY RISK.AND IT WILL LEAD TO THE TOTAL FAILURE OF THE ELECTRICAL EQUIPMENT. | SUPPLY FAILURE, OPEN CIRCUIT | FIRE HORN | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | RISK RANK 4 | RISK RANK 4 (ACCEPTABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | FUNCTION TEST | PERFORM FUNCTIONAL TEST OF FIRE HORN STROBE BY FORCING THE OUTPUT FROM THE FIRE AND GAS PANEL OR TEST BUTTON. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 1 | YEAR(S)
HORN, AUDIBLE | TO GIVE VISUAL OR SOUND INDICATION FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} IN CASE OF EMERGENCY. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | IN CASE OF SPURIOUS OPERATION OF AUDIBLE HORN {EQUIPMENT TAG NUMBER}, IT WILL NOT GIVE VISUAL OR SOUND INDICATION FOR FIRE OR EMERGENCY, WHICH IS A SAFETY RISK OR IT WILL GIVE WRONG INDICATION. AND AS A RESULT OF SPURIOUS OPERATION TOTAL FAILURE OF ELECTRICAL EQUIPMENT MAY OCCUR. | SHORT CIRCUIT, IMPROPER SUPPLY | FIRE HORN | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | RISK RANK 4 | RISK RANK 4 (ACCEPTABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | CHECK THAT THE FIRE HORN STROBE IS IN GOOD CONDITION/NO PHYSICAL DAMAGE AND FREE FROM DIRT/CONTAMINANTS, OBSTRUCTIONS OR SALT ACCUMULATION AND ANY SPLASH OF WATER ETC. IF REQUIRED CLEAN AS NECESSARY INSPECT WIRING FOR CRACKED, BROKEN, OR DETERIORATED INSULATION AND EXPOSED CONDUCTOR AND LABELS FOR DEGRADATION | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
BEACON, FLASHING | TO GIVE/PROVIDE VISUAL ALARM (FLASHING) WHEN FLAMMABLE FLUID IS SENSED BY A DETECTOR CONNECTED TO IT. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | FAIL TO FUNCTION ON DEMAND OF FLASHING BEACON {EQUIPMENT TAG NUMBER} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL NOT GIVE INDICATION DURING THE EMERGENCY CONDITIONS. | LAMP FAULTY, FUSE BLOWN, OPEN CIRCUIT, CONTACTOR FAULTY, TIMERS OR SWITCHES FAULT, ACCUMULATION ON LENS, PLC O/P MODULE FAULTY. | SPARE LAMPS, FUSE, CONTACTOR, SWITCHES, SWITCHES, TIMERS, LENS & COVER, PLC O/P MODULE. | 4 | D | RISK RANK 3 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | OVI | OPERATOR VISUAL INSPECTION | INSPECT BEACON/STROBE FOR MALFUNCTIONING OR ANY FAILURE. FOR DETAILS, REFER TO PMR. | CMT-CONDITION MONITORING TASK | OCM-OPERATOR CONDITION MONITORING | OPR-OPERATIONS | ON | 12 | MONTH(S)
BEACON, FLASHING | TO GIVE/PROVIDE VISUAL ALARM (FLASHING) WHEN FLAMMABLE FLUID IS SENSED BY A DETECTOR CONNECTED TO IT. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF BREAKDOWN. | BREAKDOWN | CRITICAL | BRD | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | BREAKDOWN OF FLASHING BEACON {EQUIPMENT TAG NUMBER} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL NOT GIVE INDICATION DURING THE EMERGENCY CONDITIONS. | LAMP FAULTY, SHORT CIRCUIT, AGING. | LAMP, LENS & COVER. | 4 | E | RISK RANK 3 | 4 | F | RISK RANK 4 | 4 | E | RISK RANK 3 | 4 | F | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | OVI | OPERATOR VISUAL INSPECTION | INSPECT BEACON/STROBE FOR MALFUNCTIONING OR ANY FAILURE. FOR DETAILS, REFER TO PMR. | CMT-CONDITION MONITORING TASK | OCM-OPERATOR CONDITION MONITORING | OPR-OPERATIONS | ON | 12 | MONTH(S)
SOUNDER/BEACON | TO GIVE/PROVIDE VISUAL ALARM WHEN FLAMMABLE GAS IS SENSED BY A DETECTOR CONNECTED TO IT. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | FAIL TO FUNCTION ON DEMAND OF COMBINED SOUNDER/BEACON {EQUIPMENT TAG NUMBER} FOR FIRE AND {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL NOT GIVE INDICATION DURING THE EMERGENCY CONDITIONS. | LAMP FAULTY, FUSE BLOWN, OPEN CIRCUIT, CONTACTOR FAULTY, TIMERS OR SWITCHES FAULT, ACCUMULATION ON LENS, PLC O/P MODULE FAULTY. | SPARE LAMPS, FUSE, CONTACTOR, SWITCHES, SWITCHES, TIMERS, LENS & COVER, PLC O/P MODULE. | 4 | D | RISK RANK 3 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | OVI | OPERATOR VISUAL INSPECTION | INSPECT BEACON/STROBE FOR MALFUNCTIONING OR ANY FAILURE. FOR DETAILS, REFER TO PMR. | CMT-CONDITION MONITORING TASK | OCM-OPERATOR CONDITION MONITORING | OPR-OPERATIONS | ON | 12 | MONTH(S)
SOUNDER/BEACON | TO GIVE/PROVIDE VISUAL ALARM WHEN FLAMMABLE GAS IS SENSED BY A DETECTOR CONNECTED TO IT. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF BREAKDOWN. | BREAKDOWN | CRITICAL | BRD | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | BREAKDOWN OF COMBINED SOUNDER/BEACON {EQUIPMENT TAG NUMBER} FOR FIRE AND {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL NOT GIVE INDICATION DURING THE EMERGENCY CONDITIONS. | LAMP FAULTY, SHORT CIRCUIT, AGING. | LAMP, LENS & COVER. | 4 | E | RISK RANK 3 | 4 | F | RISK RANK 4 | 4 | E | RISK RANK 3 | 4 | F | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | OVI | OPERATOR VISUAL INSPECTION | INSPECT BEACON/STROBE FOR MALFUNCTIONING OR ANY FAILURE. FOR DETAILS, REFER TO PMR. | CMT-CONDITION MONITORING TASK | OCM-OPERATOR CONDITION MONITORING | OPR-OPERATIONS | ON | 12 | MONTH(S)
INDICATOR, POSITION | TO INDICATE INFORMATION ABOUT POSITION OF {SERVICE} IN {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} EQUIPMENT AND FLOWLINES. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF POSITION INDICATOR {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WILL NOT BE ABLE TO GIVE ANY INFORMATION REGARDING POSITION OF {SERVICE} IN {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
INDICATOR, POSITION | TO INDICATE INFORMATION ABOUT POSITION OF {SERVICE} IN {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} EQUIPMENT AND FLOWLINES. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS OF POSITION INDICATOR {EQUIPMENT TAG NUMBER} GIVES VAGUE INFORMATION REGARDING POSITION OF {SERVICE} IN {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
INDICATOR, TEMPERATURE | TO INDICATE TEMPERATURE OF {SERVICE} FOR THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF TEMPERATURE INDICATOR {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WILL NOT BE ABLE TO GIVE ANY INFORMATION REGARDING TEMPERATURE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
INDICATOR, TEMPERATURE | TO INDICATE TEMPERATURE OF {SERVICE} FOR THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS OF TEMPERATURE INDICATOR {EQUIPMENT TAG NUMBER} GIVES VAGUE INFORMATION REGARDING TEMPERATURE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
INDICATOR, FLOW | TO INDICATE THE FLOW OF {SERVICE} OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF FLOW INDICATOR {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WILL NOT BE ABLE TO GIVE ANY INFORMATION REGARDING FLOW OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
INDICATOR, FLOW | TO INDICATE THE FLOW OF {SERVICE} OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS OF FLOW INDICATOR {EQUIPMENT TAG NUMBER} GIVES VAGUE INFORMATION REGARDING FLOW OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
GAUGE, TEMPERATURE | TO INDICATE THE TEMPERATURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF TEMPERATURE GAUGE {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WILL NOT BE ABLE TO GIVE ANY INFORMATION REGARDING TEMPERATURE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
GAUGE, TEMPERATURE | TO INDICATE THE TEMPERATURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS OF TEMPERATURE GAUGE {EQUIPMENT TAG NUMBER} GIVES VAGUE INFORMATION REGARDING TEMPERATURE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
INDICATOR, MISCELLANEOUS | TO INDICATE/ANALYSE THE OPERATING PARAMETERS IN {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF INDICATOR {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WILL NOT BE ABLE TO GIVE ANY INFORMATION REGARDING OPERATING PARAMETRS OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
INDICATOR, MISCELLANEOUS | TO INDICATE/ANALYSE THE OPERATING PARAMETERS IN {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS OF INDICATOR {EQUIPMENT TAG NUMBER} GIVES VAGUE INFORMATION REGARDING OPERATING PARAMETRS OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, LEVEL CONTROL | TO MAINTAIN A CONSTANT LEVEL IN A LIQUID/FLUID SUPPLY OR TO REGULATE THE FLOW INTO THE LIQUID SUPPLY WHICH MAINTAINS A CONSTANT LEVEL TO MEET THE USAGE DEMANDS FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-PROCESS MEDIUM. | EXTERNAL LEAKAGE-PROCESS MEDIUM | DEGRADED | ELP | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | EXTERNAL LEAKAGE OF LEVEL CONTROL VALVE {EQUIPMENT TAG NUMBER} CAN LEAD TO THE UNWANTED PRESSURE DROP ACROSS THE VALVE, WHICH MAY CAUSE DISTURBANCE IN OPERATION AND ENVIRONMENTAL CONSEQUENCES MAY HAPPEN. | LOOSENESS | STEM | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 2 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENT/ACTION TO MITIGATE THE LEAKAGE. CHECK FOR BOLTS TIGHTNESS. REPLACE CONSUMABLES LIKE GASKETS, O-RINGS ETC. (FOR DETAIL, REFER TO PMR) | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, LEVEL CONTROL | TO MAINTAIN A CONSTANT LEVEL IN A LIQUID/FLUID SUPPLY OR TO REGULATE THE FLOW INTO THE LIQUID SUPPLY WHICH MAINTAINS A CONSTANT LEVEL TO MEET THE USAGE DEMANDS FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-UTILITY MEDIUM. | EXTERNAL LEAKAGE-UTILITY MEDIUM | DEGRADED | ELU | NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | EXTERNAL LEAKAGE-UTILITY MEDIUM CAN LEAD TO THE ABRUPT/UNWANTED CHANGE IN THE LEVEL CONTROL VALVE {EQUIPMENT TAG NUMBER} STATE AND THUS LIMITING THE VALVE TO PERFORM TASK EFFICIENTLY. | MECHANICAL FAILURE-GENERAL | SUBUNIT | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 4 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENTS/ACTION TO MITIGATE THE LEAKAGE. REPLACE CONSUMABLES LIKE GASKETS, O RINGS ETC. (FOR DETAIL, REFER TO PMR) | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, LEVEL CONTROL | TO MAINTAIN A CONSTANT LEVEL IN A LIQUID/FLUID SUPPLY OR TO REGULATE THE FLOW INTO THE LIQUID SUPPLY WHICH MAINTAINS A CONSTANT LEVEL TO MEET THE USAGE DEMANDS FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF PLUGGED/CHOKED. | PLUGGED/CHOKED | DEGRADED | PLU | AGE-RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | IF LEVEL CONTROL VALVE {EQUIPMENT TAG NUMBER} PLUGGED/CHOKED DUE TO FOREIGN MATERIAL, IT WOULD NOT WORK PROPERLY AND ULTIMATELY IT WILL LEAD TO PROCESS AT RISK. | BLOCKAGE/PLUGGED | CLOSURE MEMBER (BALL/GATE/DISC/ETC.) | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.12 | 0.76 | 1.86 | 150.1973 | - | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | PERFORM MAJOR OVERHAULING OF THE VALVE, SEAT DISC LAPPING, CLEANING AND SERVICING OF VALVE INTERNALS, AND REPLACEMENT OF ALL SEALS/SOFT GOODS. PERFORM LEAK TEST OF THE VALVE AND ENSURE THAT VALVE CONFORMS TO THE DESIGN VALVE LEAKAGE CLASSIFICATION AS SET OUT IN THE VALVE TAG PLATE OR DATASHEET. ENSURE THE CONTROL VALVE COMPONENTS AND ASSOCIATED CABLING ARE IN GOOD CONDITION, SECURELY FITTED AND FIT FOR PURPOSE. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 36 | MONTH(S)
VALVE, LEVEL CONTROL | TO MAINTAIN A CONSTANT LEVEL IN A LIQUID/FLUID SUPPLY OR TO REGULATE THE FLOW INTO THE LIQUID SUPPLY WHICH MAINTAINS A CONSTANT LEVEL TO MEET THE USAGE DEMANDS FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF VALVE LEAKAGE IN CLOSED POSITION. | VALVE LEAKAGE IN CLOSED POSITION | CRITICAL | LCP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF VALVE LEAKAGE IN CLOSED POSITION OF LEVEL CONTROL VALVE {EQUIPMENT TAG NUMBER} EXCEEDS THAN ACCEPTABLE LEAKAGE RATE, SO IT WOULD NOT BE POSSIBLE TO CONTROL THE PROCESS, WHICH RESULT AS PROCESS DISTURBANCE. | LOOSENESS, CORROSION, INSTRUMENT FAILURE-GENERAL | PACKING, SEAT RINGS, SUBUNIT | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 10 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | PERFORM MAJOR OVERHAULING OF THE VALVE, SEAT DISC LAPPING, CLEANING AND SERVICING OF VALVE INTERNALS, AND REPLACEMENT OF ALL SEALS/SOFT GOODS. PERFORM LEAK TEST OF THE VALVE AND ENSURE THAT VALVE CONFORMS TO THE DESIGN VALVE LEAKAGE CLASSIFICATION AS SET OUT IN THE VALVE TAG PLATE OR DATASHEET. ENSURE THE CONTROL VALVE COMPONENTS AND ASSOCIATED CABLING ARE IN GOOD CONDITION, SECURELY FITTED AND FIT FOR PURPOSE. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 36 | MONTH(S)
VALVE, LEVEL CONTROL | TO MAINTAIN A CONSTANT LEVEL IN A LIQUID/FLUID SUPPLY OR TO REGULATE THE FLOW INTO THE LIQUID SUPPLY WHICH MAINTAINS A CONSTANT LEVEL TO MEET THE USAGE DEMANDS FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO REGULATE. | FAIL TO REGULATE | CRITICAL | FTR | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF LEVEL CONTROL VALVE {EQUIPMENT TAG NUMBER} FAIL TO REGULATE, IT WOULD NOT BE POSSIBLE TO CONTROL/KEEP THE PROCESS AT A SET POINT, THIS MAY LEADS TO PROCESS DISTURBANCE. | BLOCKAGE/PLUGGED, INSTRUMENT FAILURE-GENERAL | VALVE BODY W/INTERNALS | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.28 | 1.14 | 2.46 | 100.1316 | 2.7 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT FOR ACTUATOR AND ALL THE TUBING CONNECTIONS FOR UTILITY LEAKAGE AND CHECK POSITIONER FEEDBACK LINK FOR LOOSENESS. ENSURE THAT PROPER INSTRUMENT AIR SUPPLY IS PROVIDING TO POSITIONER AND ACTUATOR AS PER DATA SHEET. ENSURE THAT STEM COUPLING (STEM CONNECTOR) OF ACTUATOR AND VALVE BODY IS TIGHTENED AND PROPERLY ADJUSTED. PERFORM LUBRICATION OF VALVE AND GEARBOX(IF PRESENT). CHECK VALVE TRAVEL IS SAME AS VALVE DATA PLATE. IF THE VALVE STEM TRAVEL INDICATION DIDN’T SHOW CORRECTLY 0% OR 100% TRAVEL AND ANY OFFSET FOUND, PERFORM CALIBRATION OF THE VALVE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 12 | MONTH(S)
SWITCH, PRESSURE | TO MAKE CONTACT EITHER ON PRESSURE RISE OR ON PRESSURE FALL FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE WILL HAPPEN IN CASE OF ABNORMAL OUTPUT-LOW. | ABNORMAL OUTPUT-LOW | CRITICAL | AOL | AGE-RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | ABNORMAL OUTPUT-LOW OF PRESSURE SWITCH {EQUIPMENT TAG NUMBER} WILL PROVIDE THE FALSE FEEDBACK IN COMPARISON TO ITS SET VALUE WHICH MAY CAUSE PROCESS DISTURBANCE. | OUT OF ADJUSTMENT | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.29 | 1.4 | 393.4205 | 4 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | FUNCTION TEST AND CALIBRATION | VISUALLY INSPECT THE SWITCH FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ANY DUST, MOISTURE INSIDE TERMINAL HOUSING. INSPECT THE SWITCH BODY FOR DAMAGE. CHECK RESISTANCE OF CONTACTS. CARRY OUT TIGHTENING OF ALL CONNECTIONS. PERFORM CALIBRATION, IF READINGS DRIFT. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 24 | MONTH(S)
SWITCH, PRESSURE | TO MAKE CONTACT EITHER ON PRESSURE RISE OR ON PRESSURE FALL FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF PRESSURE SWITCH {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WILL NOT ABLE TO PROVIDE ANY FEEDBACK OF PRESSURE TO ITS CONTROL ELEMENT WHICH MAY LEADS TO PROCESS INTERRUPTION. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | FUNCTION TEST AND CALIBRATION | CHECK FOR ADEQUATE SUPPLY VOLTAGES. CHECK SWITCH CONTACTS AND POWER SUPPLY TERMINALS ARE NOT PITTED OR OXIDIZED. CARRY OUT TIGHTENING OF ALL CONNECTIONS. CHECK RESISTANCE OF CONTACTS. CHECK THE SWITCHING ACTION BY SIMULATING THE INPUT SIGNAL. ENSURE DEAD BAND IS IN RANGE AS SPECIFIED IN DATA SHEET. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 24 | MONTH(S)
SWITCH, PRESSURE | TO MAKE CONTACT EITHER ON PRESSURE RISE OR ON PRESSURE FALL FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS IN PRESSURE SWITCH {EQUIPMENT TAG NUMBER} CAN CAUSE DISTURBANCE IN MEASURING DESIRED VALUE/OUTPUT RESULTING IN UNSTABLE OPERATION. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | FUNCTION TEST AND CALIBRATION | VISUALLY INSPECT THE SWITCH HOUSING AND CABLE ENTRIES FOR ANY DAMAGE OR INGRESS AND TIGHTEN THE TERMINAL SCREWS. CHECK FOR ANY DUST, MOISTURE INSIDE TERMINAL HOUSING. ENSURE O-RING/SEALS ARE CLEAN AND INTACT. VISUALLY INSPECT THE CONDITION OF THE SWITCHING MECHANISM. PERFORM FUNCTION TEST, IF REQUIRED. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 24 | MONTH(S)
SWITCH, PRESSURE | TO MAKE CONTACT EITHER ON PRESSURE RISE OR ON PRESSURE FALL FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | SPURIOUS OPERATION OF PRESSURE SWITCH {EQUIPMENT TAG NUMBER} MAY GIVE FALSE FEEDBACK TO CONTROL SYSTEM AND CAUSE THE PROCESS DISTURBANCE. | BLOCKAGE/PLUGGED, FAULTY SIGNAL/INDICATION/ALARM, INSTRUMENT FAILURE-GENERAL, NO SIGNAL/INDICATION/ALARM | ELECTRONICS (CONDITIONING), SENSING ELEMENT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.58 | 1.47 | 3.09 | 77.6531 | 2.2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | FUNCTION TEST AND CALIBRATION | CHECK FOR ANY DUST, MOISTURE INSIDE TERMINAL HOUSING. CHECK SWITCH CONTACTS AND POWER SUPPLY TERMINALS ARE NOT PITTED OR OXIDIZED. CARRY OUT TIGHTENING OF ALL CONNECTIONS AND CHECK THE RESISTANCE OF CONTACTS. ENSURE THAT SWITCHING MECHANISM AND TRIP SETTING IS IN TOLERABLE RANGE AS SPECIFIED IN DATA SHEET. IF ANY VARIATION FOUND, PERFORM CALIBRATION. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 24 | MONTH(S)
SWITCH, FLOW | TO MEASURE AND CONTROL THE LIQUID FLOW FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | IF FLOW SWITCH {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WILL NOT ABLE TO PROVIDE ANY FEEDBACK OF FLOW TO ITS CONTROL ELEMENT. | BLOCKAGE/PLUGGED | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | RISK RANK 4 | RISK RANK 4 (ACCEPTABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENT TO MITIGATE THE PROBLEM. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
SWITCH, FLOW | TO MEASURE AND CONTROL THE LIQUID FLOW FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | SPURIOUS OPERATION OF FLOW SWITCH {EQUIPMENT TAG NUMBER} MAY GIVE FALSE FEEDBACK TO CONTROL SYSTEM. | BLOCKAGE/PLUGGED | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | RISK RANK 4 | RISK RANK 4 (ACCEPTABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENT TO MITIGATE THE PROBLEM. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
SWITCH, FLOW | TO MEASURE AND CONTROL THE LIQUID FLOW FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | MINOR IN-SERVICE PROBLEMS IN FLOW SWITCH {EQUIPMENT TAG NUMBER} CAN CAUSE DISTURBANCE IN MEASURING DESIRED VALUE/OUTPUT RESULTING IN UNSTABLE OPERATION. | FAULTY SIGNAL/INDICATION/ALARM | SENSING ELEMENT, OTHER | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | RISK RANK 4 | RISK RANK 4 (ACCEPTABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENT TO MITIGATE THE PROBLEM. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
SWITCH, TEMPERATURE | TO MEASURE AND CONTROL THE TEMPERATURE FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE WILL HAPPEN IN CASE OF ABNORMAL OUTPUT-LOW. | ABNORMAL OUTPUT-LOW | CRITICAL | AOL | AGE-RELATED | EVIDENT | PROCESS AND OPERATIONAL | ABNORMAL OUTPUT-LOW OF TEMPERATURE SWITCH {EQUIPMENT TAG NUMBER} WILL NOT GIVE FEEDBACK, IF PROCESS SET LIMIT IS REACHED THAT MAY IMPACT THE PERFORMANCE OF CORRESPONDING EQUIPMENT. | OUT OF ADJUSTMENT | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.29 | 1.4 | 393.4205 | 4 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | FUNCTION TEST AND CALIBRATION | CHECK SWITCH CONTACTS AND POWER SUPPLY TERMINALS ARE NOT PITTED OR OXIDIZED. CHECK FOR ANY DUST, MOISTURE INSIDE TERMINAL HOUSING. PERFORM TERMINAL TIGHTENING. IF SET POINT OR DEAD BAND IS OUT, PERFORM CALIBRATION OF SWITCH. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 36 | MONTH(S)
SWITCH, TEMPERATURE | TO MEASURE AND CONTROL THE TEMPERATURE FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS OF TEMPERATURE SWITCH {EQUIPMENT TAG NUMBER} WILL GIVE ERRATIC FEEDBACK OF TEMPERATURE, WHICH MAY GENERATE UNNECESSARY ALARM/TRIPPING AND MAY CAUSE PROCESS DISTURBANCE. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | FUNCTION TEST AND CALIBRATION | VISUALLY INSPECT THE SWITCH HOUSING AND CABLE ENTRIES FOR ANY DAMAGE. TIGHTEN ALL TERMINALS. VISUALLY INSPECT THE CONDITION OF THE SWITCHING MECHANISM. IF SET POINT OR DEAD BAND IS OUT, PERFORM CALIBRATION OF SWITCH. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 36 | MONTH(S)
SWITCH, TEMPERATURE | TO MEASURE AND CONTROL THE TEMPERATURE FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | SPURIOUS OPERATION OF TEMPERATURE SWITCH {EQUIPMENT TAG NUMBER} MAY GIVE FALSE FEEDBACK AND CAN INITIATES UNNECESSARY ALARMS/TRIPPING. | BLOCKAGE/PLUGGED, FAULTY SIGNAL/INDICATION/ALARM, INSTRUMENT FAILURE-GENERAL, NO SIGNAL/INDICATION/ALARM | ELECTRONICS (CONDITIONING), SENSING ELEMENT | 5 | E | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.58 | 1.47 | 3.09 | 77.6531 | 2.2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | FUNCTION TEST AND CALIBRATION | INSPECT THAT THERE WOULD BE NO EVIDENCE OF DAMAGE TO CABLES, GLANDS. CHECK FOR NO EVIDENCE OF DAMAGE TO THE BODY OR CORROSION TO ANY OF THE COMPONENTS OF SWITCH. CARRY OUT TIGHTENING OF ALL CONNECTIONS. CARRY OUT A FUNCTION TEST OF THE TEMPERATURE SWITCH. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 36 | MONTH(S)
SWITCH, VIBRATION | TO MEASURE AND CONTROL VIBRATION ON EQUIPMENT OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF VIBRATION SWITCH HIGH {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WILL NOT GIVE FEEDBACK IF VIBRATION REACHED TO THE SET LIMIT WHICH WILL RESULT IN THE PROCESS INTERRUPTION AT {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | BLOCKAGE/PLUGGED | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | RISK RANK 4 | RISK RANK 4 (ACCEPTABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENT TO MITIGATE THE PROBLEM. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
SWITCH, VIBRATION | TO MEASURE AND CONTROL VIBRATION ON EQUIPMENT OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | SPURIOUS OPERATION OF VIBRATION SWITCH HIGH {EQUIPMENT TAG NUMBER} MAY GIVE FALSE FEEDBACK TO CONTROL SYSTEM. | BLOCKAGE/PLUGGED | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | RISK RANK 4 | RISK RANK 4 (ACCEPTABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENT TO MITIGATE THE PROBLEM. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
SWITCH, VIBRATION | TO MEASURE AND CONTROL VIBRATION ON EQUIPMENT OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | MINOR IN-SERVICE PROBLEMS IN VIBRATION SWITCH HIGH {EQUIPMENT TAG NUMBER} CAN CAUSE DISTURBANCE IN MEASURING DESIRED VALUE/OUTPUT RESULTING IN UNSTABLE OPERATION. | FAULTY SIGNAL/INDICATION/ALARM | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | RISK RANK 4 | RISK RANK 4 (ACCEPTABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENT TO MITIGATE THE PROBLEM. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
ORIFICE, RESTRICTION | TO MEASURE FLOW RATE, FOR REDUCING PRESSURE OR RESTRICTING FLOW FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE WILL HAPPEN IN CASE OF ABNORMAL OUTPUT-LOW. | ABNORMAL OUTPUT-LOW | CRITICAL | AOL | AGE-RELATED | EVIDENT | PROCESS AND OPERATIONAL | ABNORMAL OUTPUT-LOW OF RESTRICTION ORIFICE {EQUIPMENT TAG NUMBER} WILL GIVE IMPROPER/FALSE INFORMATION REGARDING FLOW RATE WHICH MAY CAUSE THE OPERATIONAL EFFECT. | INTERNAL EDGES DAMAGED, WEAR/EROSION, VENT/DRAIN HOLES(IF AVAILABLE) CHOKED | ORIFICE PLATE | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | RISK RANK 4 | RISK RANK 4 (ACCEPTABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION | CHECK THE ORIFICE AREA IS NOT CHOKED, IT SHOULD BE CLEANED. (FOR DETAILS REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
ORIFICE, RESTRICTION | TO MEASURE FLOW RATE, FOR REDUCING PRESSURE OR RESTRICTING FLOW FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS IN RESTRICTION ORIFICE {EQUIPMENT TAG NUMBER} CAN CAUSE DISTURBANCE IN MEASURING DESIRED VALUE/OUTPUT REGARDING FLOW RATE RESULTING IN UNSTABLE OPERATION. | DEBRIS IN VENT/DRAIN HOLES, LEAKAGE FROM FLANGES, ABRASION OR PITTING ON BORE BEVEL | ORIFICE PLATE | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | RISK RANK 4 | RISK RANK 4 (ACCEPTABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION | CHECK THE SURFACE OF ORIFICE FOR ROUGHNESS/BENDING. (FOR DETAILS REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
ELEMENT, FLOW | TO MEASURE THE FLOW OF {SERVICE} AND GIVE INFORMATION FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF FLOW ELEMENT {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WOULD NOT PROVIDE INFORMATION ABOUT PROCESS, THIS MAY LEAD TO PROCESS DISTURBANCE AND THE PRODUCTION LOSS. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | E | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | ISOLATE THE FLOW ELEMENT FROM THE PROCESS MEDIUM AND DEPRESSURIZE THROUGH THE VENT/DRAIN POINT, PRIOR TO CARRYING OUT ANY WORK. CLEAN THE V-CONE OR WASH ALL PARTS WITH PROCESS COMPATIBLE SOLVENT TO REMOVE ANY DIRT. (FOR MORE DETAILS, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 24 | MONTH(S)
ELEMENT, FLOW | TO MEASURE THE FLOW OF {SERVICE} AND GIVE INFORMATION FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS IN FLOW ELEMENT {EQUIPMENT TAG NUMBER} WILL CAUSE INACCURATE MEASUREMENT OF FLOW WHICH WILL LEAD TOWARDS PROCESS INTERRUPTION. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | ISOLATE THE FLOW ELEMENT FROM THE PROCESS MEDIUM AND DEPRESSURIZE THROUGH THE VENT/DRAIN POINT, PRIOR TO CARRYING OUT ANY WORK. CLEAN THE V-CONE OR WASH ALL PARTS WITH PROCESS COMPATIBLE SOLVENT TO REMOVE ANY DIRT. (FOR MORE DETAILS, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 24 | MONTH(S)
ELEMENT, FLOW | TO MEASURE THE FLOW OF {SERVICE} AND GIVE INFORMATION FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE WILL HAPPEN IN CASE OF ABNORMAL OUTPUT-LOW. | ABNORMAL OUTPUT-LOW | CRITICAL | AOL | AGE-RELATED | EVIDENT | PROCESS AND OPERATIONAL | ABNORMAL OUTPUT-LOW OF FLOW ELEMENT {EQUIPMENT TAG NUMBER} MAY CAUSE INACCURATE INFORMATION ABOUT FLOW RESULTING IN THE PROCESS DISTURBANCE AND THE UNSTABLE OPERATION. | OUT OF ADJUSTMENT | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.29 | 1.4 | 393.4205 | 4 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | ISOLATE THE FLOW ELEMENT FROM THE PROCESS MEDIUM AND DEPRESSURIZE THROUGH THE VENT/DRAIN POINT, PRIOR TO CARRYING OUT ANY WORK. CLEAN THE V-CONE OR WASH ALL PARTS WITH PROCESS COMPATIBLE SOLVENT TO REMOVE ANY DIRT. (FOR MORE DETAILS, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 24 | MONTH(S)
TRANSMITTER, FLOW | TO MEASURE THE FLOW OF {SERVICE} AND TRANSMIT INFORMATION FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE WILL HAPPEN IN CASE OF ABNORMAL OUTPUT-LOW. | ABNORMAL OUTPUT-LOW | CRITICAL | AOL | AGE-RELATED | EVIDENT | PROCESS AND OPERATIONAL | ABNORMAL OUTPUT-LOW OF FLOW TRANSMITTER {EQUIPMENT TAG NUMBER} WILL GIVE IMPROPER/FALSE INFORMATION REGARDING PROCESS LIQUID/RECOVERED OIL WHICH MAY CAUSE THE OPERATIONAL EFFECT. | OUT OF ADJUSTMENT | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.29 | 1.4 | 393.4205 | 4 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND CALIBRATION | VISUALLY INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ANY WATER INGRESS INSIDE THE HOUSING. CHECK FOR ADEQUATE VOLTAGES. INSPECT FLANGES, VALVE MANIFOLD AND PORTS FOR ANY LEAKAGE. ENSURE THAT BLOCK VALVES ARE FULLY OPEN AND IMPULSE LINE IS NOT CHOKED OR PLUGGED. IF ANY VARIATION FOUND IN READINGS, CARRY OUT CALIBRATION OF FLOW TRANSMITTER. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 24 | MONTH(S)
TRANSMITTER, FLOW | TO MEASURE THE FLOW OF {SERVICE} AND TRANSMIT INFORMATION FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF FLOW TRANSMITTER {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WOULDN'T GIVE ANY FEEDBACK OF FLOW TO ITS FINAL CONTROL ELEMENT WHICH MAY LEADS TO PROCESS DISTURBANCE. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | E | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK THAT NO EVIDENCE OF DAMAGE TO CABLES, TAG, LABELS AND HOUSING COVER. CHECK FOR ANY WATER INGRESS INSIDE THE HOUSING AND THE CONNECTIONS ARE FREE FROM MOISTURE AND CONTAMINATION SUCH AS RUST AND CORROSION. INSPECT FOR INTERMITTENT SHORTS. CHECK FOR ADEQUATE VOLTAGE TO THE TRANSMITTER. PERFORM FUNCTION TEST AS PER PROCEDURE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
TRANSMITTER, FLOW | TO MEASURE THE FLOW OF {SERVICE} AND TRANSMIT INFORMATION FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | MINOR IN-SERVICE PROBLEMS OF FLOW TRANSMITTER {EQUIPMENT TAG NUMBER} WILL CAUSE INACCURATE MEASUREMENT OF FLOW, WHICH MAY HAVE MINOR IMPACT ON PROCESS. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK THAT NO EVIDENCE OF DAMAGE TO CABLES, TAG, LABELS AND HOUSING COVER. VISUALLY INSPECT THE FLANGES, VALVE MANIFOLD AND PORTS FOR ANY LEAKAGE. CHECK FOR ADEQUATE VOLTAGE TO THE TRANSMITTER. CARRY OUT A FUNCTION TEST (IF REQUIRED) OF FLOW TRANSMITTER. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
TRANSMITTER, FLOW | TO MEASURE THE FLOW OF {SERVICE} AND TRANSMIT INFORMATION FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF FLOW TRANSMITTER {EQUIPMENT TAG NUMBER} CAN CAUSE UNNECESSARY ALARM AND TRIP, WHICH RESULT IN PROCESS DISTURBANCE AND EQUIPMENT SHUTDOWN. | BLOCKAGE/PLUGGED, FAULTY SIGNAL/INDICATION/ALARM, INSTRUMENT FAILURE-GENERAL, NO SIGNAL/INDICATION/ALARM | ELECTRONICS (CONDITIONING), SENSING ELEMENT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.58 | 1.47 | 3.09 | 77.6531 | 2.2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND CALIBRATION | INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK THAT NO EVIDENCE OF DAMAGE TO CABLES, TAG, LABELS AND HOUSING COVER. CHECK FOR ANY WATER INGRESS INSIDE THE HOUSING AND THE CONNECTIONS ARE FREE FROM MOISTURE. INSPECT FOR INTERMITTENT SHORTS. CHECK FOR ADEQUATE VOLTAGE TO THE TRANSMITTER. IF ANY ABNORMALITY IS FOUND IN FUNCTIONING OF TRANSMITTER, PERFORM CALIBRATION AS PER PROCEDURE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 24 | MONTH(S)
METER, FLOW | TO MEASURE THE FLOW RATE OF {SERVICE} OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | IF FLOW METER {EQUIPMENT TAG NUMBER} MOUNTED ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WOULD NOT PROVIDE INFORMATION ABOUT PROCESS, THIS MAY LEAD TO PROCESS DISTURBANCE AND THE PRODUCTION LOSS. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT, OTHER | 5 | E | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | OVERHAUL | ISOLATE THE FLOW METER FROM THE PROCESS MEDIUM AND DEPRESSURIZE THROUGH THE VENT / DRAIN POINT, PRIOR TO CARRYING OUT ANY WORK. CLEAN THE V-CONE OR WASH ALL PARTS WITH PROCESS COMPATIBLE SOLVENT TO REMOVE ANY DIRT. (FOR MORE DETAILS, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 18 | MONTH(S)
METER, FLOW | TO MEASURE THE FLOW RATE OF {SERVICE} OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS IN FLOW METER {EQUIPMENT TAG NUMBER} MOUNTED ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL CAUSE INACCURATE MEASUREMENT OF FLOW WHICH WILL LEAD TOWARDS PROCESS INTERRUPTION. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT, OTHER | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | OVERHAUL | ISOLATE THE FLOW METER FROM THE PROCESS MEDIUM AND DEPRESSURIZE THROUGH THE VENT / DRAIN POINT, PRIOR TO CARRYING OUT ANY WORK. CLEAN THE V-CONE OR WASH ALL PARTS WITH PROCESS COMPATIBLE SOLVENT TO REMOVE ANY DIRT. (FOR MORE DETAILS, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 18 | MONTH(S)
METER, FLOW | TO MEASURE THE FLOW RATE OF {SERVICE} OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE WILL HAPPEN IN CASE OF ABNORMAL OUTPUT-LOW. | ABNORMAL OUTPUT-LOW | CRITICAL | AOL | AGE-RELATED | EVIDENT | PROCESS AND OPERATIONAL | ABNORMAL OUTPUT-LOW OF FLOW METER {EQUIPMENT TAG NUMBER} MOUNTED ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} MAY CAUSE INACCURATE INFORMATION ABOUT FLOW RESULTING IN THE PROCESS DISTURBANCE AND THE UNSTABLE OPERATION. | OUT OF ADJUSTMENT | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.29 | 1.4 | 393.4205 | 4 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | OVERHAUL | ISOLATE THE FLOW METER FROM THE PROCESS MEDIUM AND DEPRESSURIZE THROUGH THE VENT / DRAIN POINT, PRIOR TO CARRYING OUT ANY WORK. CLEAN THE V-CONE OR WASH ALL PARTS WITH PROCESS COMPATIBLE SOLVENT TO REMOVE ANY DIRT. (FOR MORE DETAILS, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 18 | MONTH(S)
GAUGE, LEVEL | TO MEASURE THE LEVEL OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF LEVEL GAUGE {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WILL NOT BE ABLE TO GIVE ANY INFORMATION REGARDING LEVEL OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
GAUGE, LEVEL | TO MEASURE THE LEVEL OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS OF LEVEL GAUGE {EQUIPMENT TAG NUMBER} GIVES VAGUE INFORMATION REGARDING LEVEL OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. IT HAS NO PROCESS RELATED CONSEQUENCE. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
INDICATOR, LEVEL | TO MEASURE THE LEVEL OF {SERVICE} PRESENT IN THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF LEVEL INDICATOR {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WILL NOT BE ABLE TO GIVE ANY INFORMATION REGARDING LEVEL OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. NO PROCESS RELATED CONSEQUENCE WILL HAPPEN. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
INDICATOR, LEVEL | TO MEASURE THE LEVEL OF {SERVICE} PRESENT IN THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS OF LEVEL INDICATOR {EQUIPMENT TAG NUMBER} GIVES VAGUE INFORMATION REGARDING LEVEL OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}, IT HAS NO PROCESS RELATED CONSEQUENCE. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
GAUGE, PRESSURE | TO MEASURE THE PRESSURE CHANGES IN {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF PRESSURE GAUGE {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WILL NOT BE ABLE TO GIVE ANY INFORMATION REGARDING PRESSURE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
GAUGE, PRESSURE | TO MEASURE THE PRESSURE CHANGES IN {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS OF PRESSURE GAUGE {EQUIPMENT TAG NUMBER} GIVES VAGUE INFORMATION REGARDING PRESSURE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
INDICATOR, PRESSURE | TO MEASURE THE PRESSURE CHANGES IN {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF PRESSURE INDICATOR {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WILL NOT BE ABLE TO GIVE ANY INFORMATION REGARDING PRESSURE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
INDICATOR, PRESSURE | TO MEASURE THE PRESSURE CHANGES IN {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS OF PRESSURE INDICATOR {EQUIPMENT TAG NUMBER} GIVES VAGUE INFORMATION REGARDING PRESSURE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
INDICATOR, DIFFERENTIAL PRESSURE | TO MEASURE THE PRESSURE DIFFERENCE ACROSS {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF DIFFERENTIAL PRESSURE INDICATOR {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WILL NOT BE ABLE TO GIVE ANY INFORMATION REGARDING PRESSURE DIFFERENCE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
INDICATOR, DIFFERENTIAL PRESSURE | TO MEASURE THE PRESSURE DIFFERENCE ACROSS {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS OF DIFFERENTIAL PRESSURE INDICATOR {EQUIPMENT TAG NUMBER} GIVES VAGUE INFORMATION REGARDING PRESSURE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
ELEMENT, LEVEL | TO MEASURE THE PROCESS SUBSTANCE LEVEL ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF ABNORMAL OUTPUT-LOW. | ABNORMAL OUTPUT-LOW | CRITICAL | AOL | AGE-RELATED | EVIDENT | PROCESS AND OPERATIONAL | ABNORMAL OUTPUT-LOW OF LEVEL ELEMENT {EQUIPMENT TAG NUMBER} ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL LEAD TO FAILURE OF THE ELEMENT TO PROVIDE PROPER INFORMATION ABOUT LEVEL WHICH MAY EFFECT THE PERFORMANCE OF CORROSPONDING EQUIPMENT PERFORMANCE. | OUT OF ADJUSTMENT | SENSING ELEMENT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.06 | 1.27 | 6.02 | 89.8819 | 4 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 463 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | Y | 44045 | 1 | 5 | 114.15 | INSP | INSPECTION AND CALIBRATION | INSPECT CABLE FOR DAMAGE INTEGRITY AND LOOSE TERMINATION. INSPECT OXIDATION ON TERMINATION. PERFORM CONTINUITY CHECK OF ELEMENT WITH TRANSMITTER/JUNCTION BOX. HOOK UP HART COMMUNICATOR AT THE TRANSMITTER TEST CONNECTION, CHECK FOR LOOSE TERMINATION PUT TRANSMITTER ON THE CALIBRATOR MODE. VERIFY TRANSMITTER READING AND CALIBRATOR READING AND INTEGRITY WITH THE ELEMENT. | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 2 | YEAR(S)
ELEMENT, LEVEL | TO MEASURE THE PROCESS SUBSTANCE LEVEL ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE WILL OCCURE IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | FAIL TO FUNCTION ON DEMAND OF LEVEL ELEMENT {EQUIPMENT TAG NUMBER} ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL LEAD TO FAILURE OF THE ELEMENT TO PROVIDE PROPER INFORMATION ABOUT LEVEL WHICH MAY EFFECT THE PERFORMANCE OF CORROSPONDING EQUIPMENT PERFORMANCE. | BLOCKAGE/PLUGGED | SENSING ELEMENT | 6 | F | RISK RANK 3 | 6 | F | RISK RANK 3 | 6 | F | RISK RANK 3 | 6 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.06 | 1.27 | 6.02 | 89.8819 | 2 | 3.32 | 7.61 | 15.02 | 15 | 2.3 | 463 (OREDA 2009) | 2018-11-28 | 2023-11-27 | Y | 44045 | 1 | 43800 | 5 | 22.83 | Y | 44045 | 1 | 5 | 114.15 | PMT | INSPECTION, CALIBRATION AND FUNCTIONAL TEST | INSPECT CABLE FOR DAMAGE INTEGRITY AND LOOSE TERMINATION. INSPECT OXIDATION ON TERMINATION. PERFORM CONTINUITY CHECK OF ELEMENT WITH TRANSMITTER/JUNCTION BOX. HOOK UP HART COMMUNICATOR AT THE TRANSMITTER TEST CONNECTION, CHECK FOR LOOSE TERMINATION PUT TRANSMITTER ON THE CALIBRATOR MODE. VERIFY TRANSMITTER READING AND CALIBRATOR READING AND INTEGRITY WITH THE ELEMENT. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 2 | YEAR(S)
ELEMENT, LEVEL | TO MEASURE THE PROCESS SUBSTANCE LEVEL ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS OF LEVEL ELEMENT {EQUIPMENT TAG NUMBER} ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL LEAD TO FAILURE OF THE ELEMENT TO PROVIDE PROPER INFORMATION ABOUT LEVEL WHICH MAY EFFECT THE PERFORMANCE OF CORROSPONDING EQUIPMENT PERFORMANCE. | FAULTY SIGNAL/INDICATION/ALARM | SENSING ELEMENT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.06 | 1.27 | 6.02 | 89.8819 | 3 | 3.32 | 7.61 | 15.02 | 15 | 2.3 | 463 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | Y | 44045 | 1 | 5 | 114.15 | PMT | INSPECTION, CALIBRATION AND FUNCTIONAL TEST | INSPECT CABLE FOR DAMAGE INTEGRITY AND LOOSE TERMINATION. INSPECT OXIDATION ON TERMINATION. PERFORM CONTINUITY CHECK OF ELEMENT WITH TRANSMITTER/JUNCTION BOX. HOOK UP HART COMMUNICATOR AT THE TRANSMITTER TEST CONNECTION, CHECK FOR LOOSE TERMINATION PUT TRANSMITTER ON THE CALIBRATOR MODE. VERIFY TRANSMITTER READING AND CALIBRATOR READING AND INTEGRITY WITH THE ELEMENT. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 2 | YEAR(S)
ELEMENT, TEMPERATURE | TO MEASURE THE TEMPERATURE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE WILL HAPPEN IN CASE OF ABNORMAL OUTPUT-LOW. | ABNORMAL OUTPUT-LOW | CRITICAL | AOL | AGE-RELATED | EVIDENT | PROCESS AND OPERATIONAL | ABNORMAL OUTPUT-LOW OF TEMPERATURE ELEMENT {EQUIPMENT TAG NUMBER} MAY GIVE IMPROPER INFORMATION TO ITS CORRESPONDING EQUIPMENT {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}, WHICH MAY CAUSE FALSE TRIPPING AND EFFECT THE EQUIPMENT'S PEROFRMANCE. | OUT OF ADJUSTMENT | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.29 | 1.4 | 393.4205 | 4 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | OVI | OPERATOR VISUAL INSPECTION | INSPECT CABLE FOR DAMAGE INTEGRITY AND LOOSE TERMINATION. INSPECT OXIDATION ON TERMINATION. PERFORM CONTINUITY CHECK OF ELEMENT WITH JUNCTION BOX. (FOR DETAIL, REFER TO PMR) | CMT-CONDITION MONITORING TASK | OCM-OPERATOR CONDITION MONITORING | OPR-OPERATIONS | ON | 24 | MONTH(S)
ELEMENT, TEMPERATURE | TO MEASURE THE TEMPERATURE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF TEMPERATURE ELEMENT {EQUIPMENT TAG NUMBER} WOULD NOT GIVE CORRECT TEMPERATURE VALUE WHICH MAY EFFECT THE EFFICIENCY OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | BLOCKAGE/PLUGGED, FAULTY SIGNAL/INDICATION/ALARM, INSTRUMENT FAILURE-GENERAL, NO SIGNAL/INDICATION/ALARM | ELECTRONICS (CONDITIONING), SENSING ELEMENT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.58 | 1.47 | 3.09 | 77.6531 | 2.2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | OVI | OPERATOR VISUAL INSPECTION | INSPECT CABLE FOR DAMAGE INTEGRITY AND LOOSE TERMINATION. INSPECT OXIDATION ON TERMINATION. PERFORM CONTINUITY CHECK OF ELEMENT WITH JUNCTION BOX. (FOR DETAIL, REFER TO PMR) | CMT-CONDITION MONITORING TASK | OCM-OPERATOR CONDITION MONITORING | OPR-OPERATIONS | ON | 24 | MONTH(S)
ELEMENT, TEMPERATURE | TO MEASURE THE TEMPERATURE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS OF TEMPERATURE ELEMENT {EQUIPMENT TAG NUMBER} MAY CAUSE FALSE TRIPPING AND EFFECT THE EQUIPMENT PERFORMANCE. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | OVI | OPERATOR VISUAL INSPECTION | INSPECT CABLE FOR DAMAGE INTEGRITY AND LOOSE TERMINATION. INSPECT OXIDATION ON TERMINATION. PERFORM CONTINUITY CHECK OF ELEMENT WITH JUNCTION BOX. (FOR DETAIL, REFER TO PMR) | CMT-CONDITION MONITORING TASK | OCM-OPERATOR CONDITION MONITORING | OPR-OPERATIONS | ON | 24 | MONTH(S)
TRANSMITTER, DIFFERENTIAL PRESSURE | TO MEASURE THE PRESSURE DIFFERENCE OF {SERVICE} AND TRANSMIT INFORMATION/FEEDBACK TO THE CONTROLLER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE WILL HAPPEN IN CASE OF ABNORMAL OUTPUT-LOW. | ABNORMAL OUTPUT-LOW | CRITICAL | AOL | AGE-RELATED | EVIDENT | PROCESS AND OPERATIONAL | ABNORMAL OUTPUT-LOW OF DIFFERENTIAL PRESSURE TRANSMITTER {EQUIPMENT TAG NUMBER} WILL GIVE IMPROPER/FALSE INFORMATION REGARDING PROCESS LIQUID/RECOVERED OIL WHICH MAY CAUSE THE OPERATIONAL EFFECT. | OUT OF ADJUSTMENT | SENSING ELEMENT | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.29 | 1.4 | 393.4205 | 4 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND CALIBRATION | VISUALLY INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ANY WATER INGRESS INSIDE THE HOUSING. INSPECT FOR INTERMITTENT SHORTS. CHECK FOR ADEQUATE VOLTAGE TO THE TRANSMITTER. VISUALLY INSPECT THE IMPULSE LINES FOR DAMAGE OR LEAKAGE. CARRY OUT CALIBRATION OF TRANSMITTER. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 12 | MONTH(S)
TRANSMITTER, DIFFERENTIAL PRESSURE | TO MEASURE THE PRESSURE DIFFERENCE OF {SERVICE} AND TRANSMIT INFORMATION/FEEDBACK TO THE CONTROLLER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF DIFFERENTIAL PRESSURE TRANSMITTER {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND. IT WILL NOT GIVE INDICATION / VALUE OF PROCESS LIQUID/RECOVERED OIL PRESSURE TO CONTROLLER. IT MAY LEAD TO UNSTABLE OPERATION. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | E | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ANY WATER INGRESS INSIDE THE HOUSING AND THE CONNECTIONS ARE FREE FROM MOISTURE AND CONTAMINATION SUCH AS RUST AND CORROSION. INSPECT FOR INTERMITTENT SHORTS. CHECK FOR ADEQUATE VOLTAGE TO THE TRANSMITTER. ENSURE THAT BLOCK VALVES ARE FULLY OPEN. CHECK THAT NO EVIDENCE OF DAMAGE TO CABLES, TAG, LABELS AND HOUSING COVER. CARRY OUT FUNCTION TEST OF TRANSMITTER (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 12 | MONTH(S)
TRANSMITTER, DIFFERENTIAL PRESSURE | TO MEASURE THE PRESSURE DIFFERENCE OF {SERVICE} AND TRANSMIT INFORMATION/FEEDBACK TO THE CONTROLLER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS IN DIFFERENTIAL PRESSURE TRANSMITTER {EQUIPMENT TAG NUMBER} MAY CAUSE DISTURBANCE IN MEASURING VALUE / OUTPUT OF PROCESS LIQUID/RECOVERED OIL PRESSURE RESULTING IN UNSTABLE OPERATION. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK THAT POWER SUPPLY TERMINALS ARE NOT PITTED AND OXIDIZED. TIGHTEN ALL TERMINALS. VISUALLY INSPECT THE FLANGES, VALVE MANIFOLD AND PORTS FOR ANY LEAKAGE. CARRY OUT A FUNCTION TEST OF TRANSMITTER. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 12 | MONTH(S)
TRANSMITTER, DIFFERENTIAL PRESSURE | TO MEASURE THE PRESSURE DIFFERENCE OF {SERVICE} AND TRANSMIT INFORMATION/FEEDBACK TO THE CONTROLLER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF DIFFERENTIAL PRESSURE TRANSMITTER {EQUIPMENT TAG NUMBER} WILL GIVE IMPROPER INFORMATION ABOUT PRESSURE OF PROCESS LIQUID/RECOVERED OIL TO CONTROLLER. RESULTING IN UNSTABLE OPERATION. | BLOCKAGE/PLUGGED, FAULTY SIGNAL/INDICATION/ALARM, INSTRUMENT FAILURE-GENERAL, NO SIGNAL/INDICATION/ALARM | ELECTRONICS (CONDITIONING), SENSING ELEMENT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.58 | 1.47 | 3.09 | 77.6531 | 2.2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND CALIBRATION | INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ANY WATER INGRESS INSIDE THE HOUSING AND THE CONNECTIONS ARE FREE FROM MOISTURE AND CONTAMINATION SUCH AS RUST AND CORROSION. INSPECT FOR INTERMITTENT SHORTS. TIGHTEN ALL TERMINALS. CHECK FOR ADEQUATE VOLTAGE TO THE TRANSMITTER. CHECK THAT NO EVIDENCE OF DAMAGE TO CABLES, TAG, LABELS AND HOUSING COVER. IF ANY ABNORMALITY IS FOUND IN FUNCTIONING OF TRANSMITTER, PERFORM THE CALIBRATION AS PER PROCEDURE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 12 | MONTH(S)
TRANSMITTER, POSITION | TO MEASURE THE PRESSURE OF {SERVICE} AND TRANSMIT INFORMATION/FEEDBACK TO THE CONTROLLER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE WILL HAPPEN IN CASE OF ABNORMAL OUTPUT-LOW. | ABNORMAL OUTPUT-LOW | CRITICAL | AOL | AGE-RELATED | EVIDENT | PROCESS AND OPERATIONAL | ABNORMAL OUTPUT-LOW OF PRESSURE TRANSMITTER {EQUIPMENT TAG NUMBER} WILL PROVIDE IMPROPER INFORMATION OF PRESSURE, WHICH MAY EFFECT THE EQUIPMENT/PROCESS PERFORMANCE/EFFICIENCY. | OUT OF ADJUSTMENT | SENSING ELEMENT | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.29 | 1.4 | 393.4205 | 4 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND CALIBRATION | VISUALLY INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ANY WATER INGRESS INSIDE THE HOUSING. INSPECT FOR INTERMITTENT SHORTS. CHECK FOR ADEQUATE VOLTAGE TO THE TRANSMITTER. VISUALLY INSPECT THE IMPULSE LINES FOR DAMAGE OR LEAKAGE. CARRY OUT CALIBRATION OF TRANSMITTER. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 24 | MONTH(S)
TRANSMITTER, POSITION | TO MEASURE THE PRESSURE OF {SERVICE} AND TRANSMIT INFORMATION/FEEDBACK TO THE CONTROLLER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF PRESSURE INDICATING TRANSMITTER {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND. IT WILL NOT GIVE INDICATION / CORRECT VALUE TO CONTROLLER. IT MAY LEAD TO UNSTABLE OPERATION. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | E | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ANY WATER INGRESS INSIDE THE HOUSING AND THE CONNECTIONS ARE FREE FROM MOISTURE AND CONTAMINATION SUCH AS RUST AND CORROSION. INSPECT FOR INTERMITTENT SHORTS. CHECK FOR ADEQUATE VOLTAGE TO THE TRANSMITTER. ENSURE THAT BLOCK VALVES ARE FULLY OPEN. CHECK THAT NO EVIDENCE OF DAMAGE TO CABLES, TAG, LABELS AND HOUSING COVER. CARRY OUT FUNCTION TEST OF TRANSMITTER (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
TRANSMITTER, POSITION | TO MEASURE THE PRESSURE OF {SERVICE} AND TRANSMIT INFORMATION/FEEDBACK TO THE CONTROLLER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS IN PRESSURE INDICATING TRANSMITTER {EQUIPMENT TAG NUMBER} MAY CAUSE DISTURBANCE IN MEASURING VALUE / OUTPUT WHICH RESULTING IN UNSTABLE OPERATION. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT, OTHER | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK THAT POWER SUPPLY TERMINALS ARE NOT PITTED AND OXIDIZED. TIGHTEN ALL TERMINALS. VISUALLY INSPECT THE FLANGES, VALVE MANIFOLD AND PORTS FOR ANY LEAKAGE. CARRY OUT A FUNCTION TEST OF TRANSMITTER. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
TRANSMITTER, POSITION | TO MEASURE THE PRESSURE OF {SERVICE} AND TRANSMIT INFORMATION/FEEDBACK TO THE CONTROLLER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF PRESSURE INDICATING TRANSMITTER {EQUIPMENT TAG NUMBER} WILL GIVE IMPROPER INFORMATION TO THE CONTROLLER WHICH RESULTING IN UNSTABLE OPERATION. | BLOCKAGE/PLUGGED, FAULTY SIGNAL/INDICATION/ALARM, INSTRUMENT FAILURE-GENERAL, NO SIGNAL/INDICATION/ALARM | ELECTRONICS (CONDITIONING), SENSING ELEMENT, OTHER | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.58 | 1.47 | 3.09 | 77.6531 | 2.2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND CALIBRATION | INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ANY WATER INGRESS INSIDE THE HOUSING AND THE CONNECTIONS ARE FREE FROM MOISTURE AND CONTAMINATION SUCH AS RUST AND CORROSION. INSPECT FOR INTERMITTENT SHORTS. TIGHTEN ALL TERMINALS. CHECK FOR ADEQUATE VOLTAGE TO THE TRANSMITTER. CHECK THAT NO EVIDENCE OF DAMAGE TO CABLES, TAG, LABELS AND HOUSING COVER. IF ANY ABNORMALITY IS FOUND IN FUNCTIONING OF TRANSMITTER, PERFORM THE CALIBRATION AS PER PROCEDURE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 24 | MONTH(S)
TRANSMITTER, PRESSURE | TO MEASURE THE PRESSURE OF {SERVICE} AND TRANSMIT INFORMATION/FEEDBACK TO THE CONTROLLER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE WILL HAPPEN IN CASE OF ABNORMAL OUTPUT-LOW. | ABNORMAL OUTPUT-LOW | CRITICAL | AOL | AGE-RELATED | EVIDENT | PROCESS AND OPERATIONAL | ABNORMAL OUTPUT-LOW OF PRESSURE TRANSMITTER {EQUIPMENT TAG NUMBER} WILL PROVIDE IMPROPER INFORMATION OF PRESSURE, WHICH MAY EFFECT THE EQUIPMENT/PROCESS PERFORMANCE/EFFICIENCY. | OUT OF ADJUSTMENT | SENSING ELEMENT | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.29 | 1.4 | 393.4205 | 4 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND CALIBRATION | VISUALLY INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ANY WATER INGRESS INSIDE THE HOUSING. INSPECT FOR INTERMITTENT SHORTS. CHECK FOR ADEQUATE VOLTAGE TO THE TRANSMITTER. VISUALLY INSPECT THE IMPULSE LINES FOR DAMAGE OR LEAKAGE. CARRY OUT CALIBRATION OF TRANSMITTER. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 12 | MONTH(S)
TRANSMITTER, PRESSURE | TO MEASURE THE PRESSURE OF {SERVICE} AND TRANSMIT INFORMATION/FEEDBACK TO THE CONTROLLER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF PRESSURE INDICATING TRANSMITTER {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND. IT WILL NOT GIVE INDICATION / CORRECT VALUE TO CONTROLLER. IT MAY LEAD TO UNSTABLE OPERATION. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | E | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ANY WATER INGRESS INSIDE THE HOUSING AND THE CONNECTIONS ARE FREE FROM MOISTURE AND CONTAMINATION SUCH AS RUST AND CORROSION. INSPECT FOR INTERMITTENT SHORTS. CHECK FOR ADEQUATE VOLTAGE TO THE TRANSMITTER. ENSURE THAT BLOCK VALVES ARE FULLY OPEN. CHECK THAT NO EVIDENCE OF DAMAGE TO CABLES, TAG, LABELS AND HOUSING COVER. CARRY OUT FUNCTION TEST OF TRANSMITTER (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 12 | MONTH(S)
TRANSMITTER, PRESSURE | TO MEASURE THE PRESSURE OF {SERVICE} AND TRANSMIT INFORMATION/FEEDBACK TO THE CONTROLLER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS IN PRESSURE INDICATING TRANSMITTER {EQUIPMENT TAG NUMBER} MAY CAUSE DISTURBANCE IN MEASURING VALUE / OUTPUT WHICH RESULTING IN UNSTABLE OPERATION. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK THAT POWER SUPPLY TERMINALS ARE NOT PITTED AND OXIDIZED. TIGHTEN ALL TERMINALS. VISUALLY INSPECT THE FLANGES, VALVE MANIFOLD AND PORTS FOR ANY LEAKAGE. CARRY OUT A FUNCTION TEST OF TRANSMITTER. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 12 | MONTH(S)
TRANSMITTER, PRESSURE | TO MEASURE THE PRESSURE OF {SERVICE} AND TRANSMIT INFORMATION/FEEDBACK TO THE CONTROLLER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF PRESSURE INDICATING TRANSMITTER {EQUIPMENT TAG NUMBER} WILL GIVE IMPROPER INFORMATION TO THE CONTROLLER WHICH RESULTING IN UNSTABLE OPERATION. | BLOCKAGE/PLUGGED, FAULTY SIGNAL/INDICATION/ALARM, INSTRUMENT FAILURE-GENERAL, NO SIGNAL/INDICATION/ALARM | ELECTRONICS (CONDITIONING), SENSING ELEMENT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.58 | 1.47 | 3.09 | 77.6531 | 2.2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND CALIBRATION | INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ANY WATER INGRESS INSIDE THE HOUSING AND THE CONNECTIONS ARE FREE FROM MOISTURE AND CONTAMINATION SUCH AS RUST AND CORROSION. INSPECT FOR INTERMITTENT SHORTS. TIGHTEN ALL TERMINALS. CHECK FOR ADEQUATE VOLTAGE TO THE TRANSMITTER. CHECK THAT NO EVIDENCE OF DAMAGE TO CABLES, TAG, LABELS AND HOUSING COVER. IF ANY ABNORMALITY IS FOUND IN FUNCTIONING OF TRANSMITTER, PERFORM THE CALIBRATION AS PER PROCEDURE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 12 | MONTH(S)
TRANSMITTER, TEMPERATURE | TO MEASURE THE TEMPERATURE OF {SERVICE} AND TRANSMIT INFORMATION/FEEDBACK TO THE CONTROLLER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE WILL HAPPEN IN CASE OF ABNORMAL OUTPUT-LOW. | ABNORMAL OUTPUT-LOW | CRITICAL | AOL | AGE-RELATED | EVIDENT | PROCESS AND OPERATIONAL | ABNORMAL OUTPUT-LOW OF TEMPERATURE TRANSMITTER {EQUIPMENT TAG NUMBER} WILL GIVE IMPROPER/FALSE INFORMATION WHICH MAY CAUSE THE OPERATIONAL EFFECT. | OUT OF ADJUSTMENT | SENSING ELEMENT | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.29 | 1.4 | 393.4205 | 4 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND CALIBRATION | VISUALLY INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ANY WATER INGRESS INSIDE THE HOUSING. INSPECT FOR INTERMITTENT SHORTS. CHECK FOR ADEQUATE VOLTAGE TO THE TRANSMITTER. VISUALLY INSPECT THE IMPULSE LINES FOR DAMAGE OR LEAKAGE. CARRY OUT CALIBRATION OF TRANSMITTER. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 24 | MONTH(S)
TRANSMITTER, TEMPERATURE | TO MEASURE THE TEMPERATURE OF {SERVICE} AND TRANSMIT INFORMATION/FEEDBACK TO THE CONTROLLER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF TEMPERATURE INDICATING TRANSMITTER {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WILL NOT GIVE INDICATION / VALUE OF TEMPERATURE TO CONTROLLER WHICH MAY RESULT IN UNSTABLE OPERATION AND CONSEQUENTLY PROCESS WILL BE DISTURBED. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | E | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ANY WATER INGRESS INSIDE THE HOUSING AND THE CONNECTIONS ARE FREE FROM MOISTURE AND CONTAMINATION SUCH AS RUST AND CORROSION. INSPECT FOR INTERMITTENT SHORTS. CHECK FOR ADEQUATE VOLTAGE TO THE TRANSMITTER. ENSURE THAT BLOCK VALVES ARE FULLY OPEN. CHECK THAT NO EVIDENCE OF DAMAGE TO CABLES, TAG, LABELS AND HOUSING COVER. CARRY OUT FUNCTION TEST OF TRANSMITTER (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
TRANSMITTER, TEMPERATURE | TO MEASURE THE TEMPERATURE OF {SERVICE} AND TRANSMIT INFORMATION/FEEDBACK TO THE CONTROLLER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS IN TEMPERATURE TRANSMITTER {EQUIPMENT TAG NUMBER} CAN CAUSE DISTURBANCE IN MEASURING DESIRED VALUE / OUTPUT OF TEMPERATURE RESULTING IN UNSTABLE OPERATION. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK THAT POWER SUPPLY TERMINALS ARE NOT PITTED AND OXIDIZED. TIGHTEN ALL TERMINALS. VISUALLY INSPECT THE FLANGES, VALVE MANIFOLD AND PORTS FOR ANY LEAKAGE. CARRY OUT A FUNCTION TEST OF TRANSMITTER. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
TRANSMITTER, TEMPERATURE | TO MEASURE THE TEMPERATURE OF {SERVICE} AND TRANSMIT INFORMATION/FEEDBACK TO THE CONTROLLER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF TEMPERATURE TRANSMITTER {EQUIPMENT TAG NUMBER} WILL RESULT IN IMPROPER TEMPERATURE INFORMATION RESULTING IN UNSTABLE OPERATION. | BLOCKAGE/PLUGGED, FAULTY SIGNAL/INDICATION/ALARM, INSTRUMENT FAILURE-GENERAL, NO SIGNAL/INDICATION/ALARM | ELECTRONICS (CONDITIONING), SENSING ELEMENT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.58 | 1.47 | 3.09 | 77.6531 | 2.2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND CALIBRATION | INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ANY WATER INGRESS INSIDE THE HOUSING AND THE CONNECTIONS ARE FREE FROM MOISTURE AND CONTAMINATION SUCH AS RUST AND CORROSION. INSPECT FOR INTERMITTENT SHORTS. TIGHTEN ALL TERMINALS. CHECK FOR ADEQUATE VOLTAGE TO THE TRANSMITTER. CHECK THAT NO EVIDENCE OF DAMAGE TO CABLES, TAG, LABELS AND HOUSING COVER. IF ANY ABNORMALITY IS FOUND IN FUNCTIONING OF TRANSMITTER, PERFORM THE CALIBRATION AS PER PROCEDURE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 24 | MONTH(S)
UNIT, DATA ACQUISITION | TO MEASURE, MANAGE AND CONTROL THE LEVEL OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF DATA ACQUISITION UNIT {EQUIPMENT TAG NUMBER} FAILS TO FUNCTION ON DEMAND, IT WOULD NOT BE ABLE TO GIVES THE DESIRED SIGNAL OUTPUT ABOUT INDICATION AND CONTROLLING THE LEVEL OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | CONFIGURATION PROBLEM, IMPROPER POWER SUPPLY, MODULE FAILURE, LOOSE WIRING CONNECTIONS | CONTROLLER | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | CHECK CONTROL UNIT AND ITS TERMINALS FOR DEGRADATION. CHECK FOR LOOSENESS OF THE TERMINAL BOX. CHECK ITS FUNCTION FOR PROPER OPERATION AND RECTIFY IF FOUND ANY ABNORMALITY. CHECK THE ON/OFF STATUS OF CONTROL UNIT, CHECK CONNECTIONS AND CONFIRM OTHER INTERLOCKS. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 6 | MONTH(S)
UNIT, DATA ACQUISITION | TO MEASURE, MANAGE AND CONTROL THE LEVEL OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF ERRATIC OUTPUT. | ERRATIC OUTPUT | DEGRADED | ERO | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF DATA ACQUISITION UNIT {EQUIPMENT TAG NUMBER} GENERATE SPIKES (HIGH/LOW VALUES) IT WILL NOT BE ABLE TO CONTROL THE LEVEL OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WHICH MAY EFFECT THE FUNCTION OF DATA ACQUISITION UNIT. AS A RESULT PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF ERRATIC OUTPUT. | CONFIGURATION PROBLEM, IMPROPER POWER SUPPLY, MODULE FAILURE, LOOSE WIRING CONNECTIONS | CONTROLLER | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | CHECK CONTROL UNIT AND ITS TERMINALS FOR DEGRADATION. CHECK FOR LOOSENESS OF THE TERMINAL BOX. CHECK ITS FUNCTION FOR PROPER OPERATION AND RECTIFY IF FOUND ANY ABNORMALITY. CHECK THE ON/OFF STATUS OF CONTROL UNIT, CHECK CONNECTIONS AND CONFIRM OTHER INTERLOCKS. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 6 | MONTH(S)
UNIT, DATA ACQUISITION | TO MEASURE, MANAGE AND CONTROL THE LEVEL OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | IN CASE OF SPURIOUS OPERATION DATA ACQUISITION UNIT {EQUIPMENT TAG NUMBER} WILL GENERATE ABNORMAL OUTPUT FOR DESIRE INSTRUMENT, WHICH MAY EFFECT THE OPERATION OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | CONFIGURATION PROBLEM, IMPROPER POWER SUPPLY, MODULE FAILURE, LOOSE WIRING CONNECTIONS | CONTROLLER | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | CHECK CONTROL UNIT AND ITS TERMINALS FOR DEGRADATION. CHECK FOR LOOSENESS OF THE TERMINAL BOX. CHECK ITS FUNCTION FOR PROPER OPERATION AND RECTIFY IF FOUND ANY ABNORMALITY. CHECK THE ON/OFF STATUS OF CONTROL UNIT, CHECK CONNECTIONS AND CONFIRM OTHER INTERLOCKS. (FOR DETAIL, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 6 | MONTH(S)
TRANSMITTER, ANALYSER | TO MEASURE/ANALYSE THE MOISTURE CONTENT PRESENT IN {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE WILL HAPPEN IN CASE OF ABNORMAL OUTPUT-LOW. | ABNORMAL OUTPUT-LOW | CRITICAL | AOL | AGE-RELATED | EVIDENT | PROCESS AND OPERATIONAL | ABNORMAL OUTPUT-LOW OF ANALYSER TRANSMITTER {EQUIPMENT TAG NUMBER} WILL GIVE IMPROPER/FALSE INFORMATION REGARDING {SERVICE} WHICH MAY CAUSE THE OPERATIONAL EFFECT. | OUT OF ADJUSTMENT | SENSING ELEMENT | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
TRANSMITTER, ANALYSER | TO MEASURE/ANALYSE THE MOISTURE CONTENT PRESENT IN {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF ANALYSER TRANSMITTER {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WOULDN'T BE ABLE TO OPTIMIZE PROCESS CONDITION. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
TRANSMITTER, ANALYSER | TO MEASURE/ANALYSE THE MOISTURE CONTENT PRESENT IN {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS IN ANALYSER TRANSMITTER {EQUIPMENT TAG NUMBER} WOULDN'T OPTIMIZE THE PROCESS PARAMETERS ACCURATELY, WHICH INDIRECTLY LEADS PROCESS DISTRUBANCE. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
TRANSMITTER, ANALYSER | TO MEASURE/ANALYSE THE MOISTURE CONTENT PRESENT IN {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF ANALYSER TRANSMITTER {EQUIPMENT TAG NUMBER} WILL GIVE IMPROPER INFORMATION ABOUT PRESSURE OF {SERVICE} TO CONTROLLER. RESULTING IN UNSTABLE OPERATION. | BLOCKAGE/PLUGGED, FAULTY SIGNAL/INDICATION/ALARM, INSTRUMENT FAILURE-GENERAL, NO SIGNAL/INDICATION/ALARM | ELECTRONICS (CONDITIONING), SENSING ELEMENT | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | TAKE CORRECTIVE ACTIONS OR PERFORM NECESSARY REPLACEMENT UPON FAILURE. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
PROPORTIONER, FOAM | TO MIX THE CORRECT AMOUNT OF WATER AND FOAM CONCENTRATE FOR PRODUCING FIRE FIGHTING FOAM. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-PROCESS MEDIUM. | EXTERNAL LEAKAGE-PROCESS MEDIUM | CRITICAL | ELP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | EXTERNAL LEAKAGE OF FOAM PROPORTIONER {EQUIPMENT TAG NUMBER} CAN LEAD TO THE UNWANTED PRESSURE DROP ACROSS THAT VALVE, PROCESS AND SAFETY RELATED CONSEQUENCES MAY OCCUR. | CORROSION, LEAKAGE, MECHANICAL FAILURE-GENERAL | BONNET, SEAT RINGS, STEM, SUBUNIT, PACKING, SEALS | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.05 | 1.12 | 3.37 | 101.9194 | 32 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION | CHECK FOR SIGNS OF DAMAGE, LEAKS, OR CORROSION. | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | WEEK(S)
PROPORTIONER, FOAM | TO MIX THE CORRECT AMOUNT OF WATER AND FOAM CONCENTRATE FOR PRODUCING FIRE FIGHTING FOAM. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO CLOSE ON DEMAND. | FAIL TO CLOSE ON DEMAND | CRITICAL | FTC | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF FOAM PROPORTIONER {EQUIPMENT TAG NUMBER} FAIL TO CLOSE ON DEMAND IT WOULD NOT BE ABLE TO CONTROL THE DESIRED PROCESS ARE REQUIREMENTS, AN OPERATIONAL EFFECT MAY OCCUR DUE TO THIS FAILURE. | BLOCKAGE/PLUGGED, STICKING, INSTRUMENT FAILURE-GENERAL, MECHANICAL FAILURE-GENERAL | VALVE BODY W/INTERNALS, PILOT VALVE, STEM, SUBUNIT, SEAT RINGS | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | 2.27 | 11.88 | 50.2863 | 2.8 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | INSPECTION AND MAINTENANCE | CHECKING AND TIGHTENING CONNECTIONS. INSPECTING VALVES AND FITTINGS FOR WEAR OR DAMAGE. VERIFYING PROPER OPERATION OF CONTROLS. CLEANING AND LUBRICATING COMPONENTS AS NECESSARY. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 6 | MONTH(S)
PROPORTIONER, FOAM | TO MIX THE CORRECT AMOUNT OF WATER AND FOAM CONCENTRATE FOR PRODUCING FIRE FIGHTING FOAM. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO OPEN ON DEMAND. | FAIL TO OPEN ON DEMAND | CRITICAL | FTO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | IF FOAM PROPORTIONER {EQUIPMENT TAG NUMBER} FAIL TO OPEN ON DEMAND THEN IT WOULD NOT BE ABLE TO GIVE SUPPLY OF FIRE FIGHTING FOAM, WHICH MAY LEADS TO THE OPERATIONAL CONSEQUENCE. | BLOCKAGE/PLUGGED, INSTRUMENT FAILURE-GENERAL, MECHANICAL FAILURE-GENERAL | PILOT VALVE, SUBUNIT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 1.08 | 3.46 | 105.4944 | 2.3 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | INSPECTION AND MAINTENANCE | CHECKING AND TIGHTENING CONNECTIONS. INSPECTING VALVES AND FITTINGS FOR WEAR OR DAMAGE. VERIFYING PROPER OPERATION OF CONTROLS. CLEANING AND LUBRICATING COMPONENTS AS NECESSARY. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 6 | MONTH(S)
PROPORTIONER, FOAM | TO MIX THE CORRECT AMOUNT OF WATER AND FOAM CONCENTRATE FOR PRODUCING FIRE FIGHTING FOAM. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF VALVE LEAKAGE IN CLOSED POSITION. | VALVE LEAKAGE IN CLOSED POSITION | CRITICAL | LCP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | VALVE LEAKAGE IN CLOSE POSITION OF THE FOAM PROPORTIONER {EQUIPMENT TAG NUMBER} MAY CAUSE PROCESS AND SAFETY HAZARD. AS A RESULT, IT WILL EFFECT THE FUNCTIONAL AND PERFORMANCE OF RELATED EQUIPMENT. | LEAKAGE, WEAR | VALVE BODY, SEAT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | 0.34 | 1.88 | 335.7353 | - | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | FLUSHING AND CLEANING SYSTEM COMPONENTS. CHECKING AND CALIBRATING EQUIPMENT. REPLACING WORN OR DETERIORATED PARTS AS NEEDED. CHECKING AND TIGHTENING CONNECTIONS. INSPECTING VALVES AND FITTINGS FOR WEAR OR DAMAGE. VERIFYING PROPER OPERATION OF CONTROLS. CLEANING AND LUBRICATING COMPONENTS AS NECESSARY. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
CONTROL PANEL, INSTRUMENT | TO MONITOR AND CONTROL THE LOGIC OPERATING SEQUENCES AND FLOW OF POWER FOR THE EQUIPMENT OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF INSTRUMENT CONTROL PANEL {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, THEN IT WILL GIVE NO FEEDBACK/CONTROL SIGNAL. AS A RESULT, IT WILL LEAD TO THE TOTAL FAILURE OF THE INSTRUMENTATION. | BREAKER FAULTY, MALFUNCTION OF CONTROL CIRCUIT, CONTROL SUPPLY FAILURE, LOOSE CONNECTIONS, ELECTRONIC CARD FAULTY (AS APPLICABLE) | BREAKER, CONTROL CIRCUIT, CONTACTOR, ELECTRONIC CARD (AS APPLICABLE) | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | OVI, PMT | OPERATOR VISUAL INSPECTION, PREVENTIVE MAINTENANCE TASK | OPERATOR VISUAL INSPECTION: INFORM PMT TO CHECK IN CASE OF ANY ABNORMALITY. PREVENTIVE MAINTENANCE: ENSURE THAT CONTROL PANEL IS FREE FROM WATER INGRESS, ACCUMULATION OF DUST, DIRT, MOISTURE AND OIL. CHECK DISPLAY FOR ANY FAULT/ALARM. REFER TO DETAILED 365 DAYS TASK LIST. | CMT-CONDITION MONITORING TASK, PMT-PREVENTIVE MAINTENANCE TASK | OCM-OPERATOR CONDITION MONITORING, PT-PREVENTIVE TASK | OPR-OPERATIONS, MAINT-MAINTENANCE TECHNICIAN | ON, OFF | 1, 720 | DAY(S), DAY(S)
CONTROL PANEL, INSTRUMENT | TO MONITOR AND CONTROL THE LOGIC OPERATING SEQUENCES AND FLOW OF POWER FOR THE EQUIPMENT OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF OVERHEATING. | OVERHEATING | DEGRADED | OHE | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | OVERHEATING OF INSTRUMENT CONTROL PANEL {EQUIPMENT TAG NUMBER} MAY CAUSE THERMAL RUNAWAY INSIDE THE PANEL, WHICH WILL LEAD TO ASSET DAMAGE. AS A RESULT OF OVERHEATING, FUNCTION AND PERFORMANCE OF THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL DISTURB AND IT MAY ALSO LEAD THE INSTRUMENTATION TO PARTIAL FAILURE. | INTERNAL COMPONENTS MALFUNCTION, DETERIORATED ASSEMBLY, LOOSE CONNECTIONS | INTERFACE COMPONENTS OF PANEL, CONNECTIONS TIGHTNESS | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | INSPECT PANEL COMPONENTS FOR ANY ABNORMALITY AND SIGN OF BURNS. CHECK DISPLAY FOR ANY ABNORMAL ALARM/FAULT. REFER TO DETAILED 365 DAYS TASK LIST. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 720 | DAY(S)
CONTROL PANEL, INSTRUMENT | TO MONITOR AND CONTROL THE LOGIC OPERATING SEQUENCES AND FLOW OF POWER FOR THE EQUIPMENT OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF THE INSTRUMENT CONTROL PANEL {EQUIPMENT TAG NUMBER} MAY LEAD TO NO SIGNAL TO / FROM HYDRAULIC {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. AS A RESULT, IT MAY LEAD TO PROCESS/PERSONAL AT RISK. AND AS A RESULT OF SPURIOUS OPERATION TOTAL FAILURE OF INSTRUMENTATION MAY OCCUR. | MALFUNCTIONING OF INPUT SENSING DEVICES & COMMUNICATION | INPUT SENSING DEVICES | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | EXAMINE EQUIPMENT FOR DAMAGE, CORROSION AND CONTAMINATION. INSPECT I/O CARDS ARE INTACT AND WORKING PROPERLY. CHECK DISPLAY FOR ANY ABNORMAL ALARM/FAULT. REFER TO DETAILED 365 DAYS TASK LIST. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 720 | DAY(S)
CONTROL PANEL, INSTRUMENT | TO MONITOR AND CONTROL THE LOGIC OPERATING SEQUENCES AND FLOW OF POWER FOR THE EQUIPMENT OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF STRUCTURAL DEFICIENCY. | STRUCTURAL DEFICIENCY | DEGRADED | STD | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | STRUCTURAL DEFICIENCY MAY CAUSE THE UNDESIRED INSTRUMENT CONTROL PANEL {EQUIPMENT TAG NUMBER} OPERATION. AS A RESULT, IT MAKES THE {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} VULNERABLE TO FAULT. STRUCTURAL DEFICIENCY OF CONTROL PANEL MAY LEAD TO THE PARTIAL FAILURE OF THE EQUIPMENT. | CABLE INSULATION/GLAND DAMAGED, INDICATION LAMP FAULTY/FUSED, PUSH BUTTON FAULTY | CABLE GLAND, INDICATION LAMP, PUSH BUTTON | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | INSPECT THE MOUNTING COMPONENTS FOR SECURITY AND REPLACE THE FAULTY COMPONENTS TO MITIGATE THE PROBLEM. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
CONTROL PANEL, FIRE & GAS | TO MONITOR AND CONTROL THE LOGIC OPERATING SEQUENCES AND FLOW OF POWER FOR THE FIRE AND ALARM EQUIPMENT OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF GENERAL CONTROL PANEL {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, THEN IT WILL GIVE NO FEEDBACK/CONTROL SIGNAL. AS A RESULT, IT WILL LEAD TO EXPANDER STOPPAGE.AND IT WILL LEAD TO THE TOTAL FAILURE OF THE ELECTRICAL EQUIPMENT. | BREAKER FAULTY, MALFUNCTION OF CONTROL CIRCUIT, CONTROL SUPPLY FAILURE, LOOSE CONNECTIONS, ELECTRONIC CARD FAULTY (AS APPLICABLE) | BREAKER, CONTROL CIRCUIT, CONTACTOR, ELECTRONIC CARD (AS APPLICABLE) | 2 | C | RISK RANK 3 | 2 | D | RISK RANK 4 | 2 | D | RISK RANK 4 | 2 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | 188.1137 | 1.8 | IEEE GOLD BOOK PAGE NO. 236 | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | OVI, PMT | OPERATOR VISUAL INSPECTION, PREVENTIVE MAINTENANCE TASK | OPERATOR VISUAL INSPECTION: INFORM PMT TO CHECK IN CASE OF ANY ABNORMALITY. PREVENTIVE MAINTENANCE: ENSURE THAT CONTROL PANEL IS FREE FROM WATER INGRESS, ACCUMULATION OF DUST, DIRT, MOISTURE AND OIL. CHECK DISPLAY FOR ANY FAULT/ALARM. REFER TO DETAILED 365 DAYS TASK LIST. | CMT-CONDITION MONITORING TASK, PMT-PREVENTIVE MAINTENANCE TASK | OCM-OPERATOR CONDITION MONITORING, PT-PREVENTIVE TASK | OPR-OPERATIONS, MAINT-MAINTENANCE TECHNICIAN | ON, OFF | 1, 2 | DAY(S), YEAR(S)
CONTROL PANEL, FIRE & GAS | TO MONITOR AND CONTROL THE LOGIC OPERATING SEQUENCES AND FLOW OF POWER FOR THE FIRE AND ALARM EQUIPMENT OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF OVERHEATING. | OVERHEATING | DEGRADED | OHE | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | OVERHEATING OF GENERAL CONTROL PANEL {EQUIPMENT TAG NUMBER} MAY CAUSE THERMAL RUNAWAY INSIDE THE PANEL, WHICH WILL LEAD TO ASSET DAMAGE. AS A RESULT OF OVERHEATING, FUNCTION AND PERFORMANCE OF THE{PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL DISTURB. AND IT MAY ALSO LEAD THE ELECTRICAL EQUIPMENT TO PARTIAL FAILURE. | INTERNAL COMPONENTS MALFUNCTION, DETERIORATED ASSEMBLY, LOOSE CONNECTIONS | INTERFACE COMPONENTS OF PANEL, CONNECTIONS TIGHTNESS | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | 2 | D | RISK RANK 4 | 2 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | 188.1137 | 1.8 | IEEE GOLD BOOK PAGE NO. 236 | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | INSPECT PANEL COMPONENTS FOR ANY ABNORMALITY AND SIGN OF BURNS. CHECK DISPLAY FOR ANY ABNORMAL ALARM/FAULT. REFER TO DETAILED 365 DAYS TASK LIST. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 2 | YEAR(S)
CONTROL PANEL, FIRE & GAS | TO MONITOR AND CONTROL THE LOGIC OPERATING SEQUENCES AND FLOW OF POWER FOR THE FIRE AND ALARM EQUIPMENT OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF THE GENERAL CONTROL PANEL {EQUIPMENT TAG NUMBER} MAY LEAD TO NO SIGNAL TO / FROM FIRE AND GAS DETECTION SYSTEM. AS A RESULT, IT MAY LEAD TO PROCESS/PERSONAL AT RISK. AND AS A RESULT OF SPURIOUS OPERATION TOTAL FAILURE OF ELECTRICAL EQUIPMENT MAY OCCUR. | MALFUNCTIONING OF INPUT SENSING DEVICES & COMMUNICATION | INPUT SENSING DEVICES | 2 | F | RISK RANK 4 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | 188.1137 | 1.8 | IEEE GOLD BOOK PAGE NO. 236 | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | EXAMINE EQUIPMENT FOR DAMAGE, CORROSION AND CONTAMINATION. INSPECT I/O CARDS ARE INTACT AND WORKING PROPERLY. CHECK DISPLAY FOR ANY ABNORMAL ALARM/FAULT. REFER TO DETAILED 365 DAYS TASK LIST. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 2 | YEAR(S)
CONTROL PANEL, FIRE & GAS | TO MONITOR AND CONTROL THE LOGIC OPERATING SEQUENCES AND FLOW OF POWER FOR THE FIRE AND ALARM EQUIPMENT OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF STRUCTURAL DEFICIENCY. | STRUCTURAL DEFICIENCY | DEGRADED | STD | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | CABLE INSULATION/GLAND DAMAGED, INDICATION LAMP FAULTY/FUSED, PUSH BUTTON FAULTY MAY CAUSE THE UNDESIRED {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} OPERATION. AS A RESULT, IT MAKES THE FIRE AND GAS DETECTION SYSTEM VULNERABLE TO FAULT. STRUCTURAL DEFICIENCY OF CONTROL PANEL MAY LEAD TO THE PARTIAL FAILURE OF THE EQUIPMENT. | CABLE INSULATION/GLAND DAMAGED, INDICATION LAMP FAULTY/FUSED, PUSH BUTTON FAULTY | CABLE GLAND, INDICATION LAMP, PUSH BUTTON | 2 | D | RISK RANK 4 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | 188.1137 | 1.8 | IEEE GOLD BOOK PAGE NO. 236 | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | INSPECT THE MOUNTING COMPONENTS FOR SECURITY AND REPLACE THE FAULTY COMPONENTS TO MITIGATE THE PROBLEM. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
CONTROL PANEL, FIRE ALARM | TO MONITOR AND CONTROL THE LOGIC OPERATING SEQUENCES AND FLOW OF POWER FOR THE FIRE AND ALARM EQUIPMENT OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF GENERAL CONTROL PANEL {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, THEN IT WILL GIVE NO FEEDBACK/CONTROL SIGNAL. AS A RESULT, IT WILL LEAD TO EXPANDER STOPPAGE.AND IT WILL LEAD TO THE TOTAL FAILURE OF THE ELECTRICAL EQUIPMENT. | BREAKER FAULTY, MALFUNCTION OF CONTROL CIRCUIT, CONTROL SUPPLY FAILURE, LOOSE CONNECTIONS, ELECTRONIC CARD FAULTY (AS APPLICABLE) | BREAKER, CONTROL CIRCUIT, CONTACTOR, ELECTRONIC CARD (AS APPLICABLE) | 2 | C | RISK RANK 3 | 2 | D | RISK RANK 4 | 2 | D | RISK RANK 4 | 2 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | 188.1137 | 1.8 | IEEE GOLD BOOK PAGE NO. 236 | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | OVI, PMT | OPERATOR VISUAL INSPECTION, PREVENTIVE MAINTENANCE TASK | OPERATOR VISUAL INSPECTION: INFORM PMT TO CHECK IN CASE OF ANY ABNORMALITY. PREVENTIVE MAINTENANCE: ENSURE THAT CONTROL PANEL IS FREE FROM WATER INGRESS, ACCUMULATION OF DUST, DIRT, MOISTURE AND OIL. CHECK DISPLAY FOR ANY FAULT/ALARM. REFER TO DETAILED 365 DAYS TASK LIST. | CMT-CONDITION MONITORING TASK, PMT-PREVENTIVE MAINTENANCE TASK | OCM-OPERATOR CONDITION MONITORING, PT-PREVENTIVE TASK | OPR-OPERATIONS, MAINT-MAINTENANCE TECHNICIAN | ON, OFF | 1, 720 | DAY(S), DAY(S)
CONTROL PANEL, FIRE ALARM | TO MONITOR AND CONTROL THE LOGIC OPERATING SEQUENCES AND FLOW OF POWER FOR THE FIRE AND ALARM EQUIPMENT OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF OVERHEATING. | OVERHEATING | DEGRADED | OHE | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | OVERHEATING OF GENERAL CONTROL PANEL {EQUIPMENT TAG NUMBER} MAY CAUSE THERMAL RUNAWAY INSIDE THE PANEL, WHICH WILL LEAD TO ASSET DAMAGE. AS A RESULT OF OVERHEATING, FUNCTION AND PERFORMANCE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL DISTURB. AND IT MAY ALSO LEAD THE ELECTRICAL EQUIPMENT TO PARTIAL FAILURE. | INTERNAL COMPONENTS MALFUNCTION, DETERIORATED ASSEMBLY, LOOSE CONNECTIONS | INTERFACE COMPONENTS OF PANEL, CONNECTIONS TIGHTNESS | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | 2 | D | RISK RANK 4 | 2 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | 188.1137 | 1.8 | IEEE GOLD BOOK PAGE NO. 236 | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | INSPECT PANEL COMPONENTS FOR ANY ABNORMALITY AND SIGN OF BURNS. CHECK DISPLAY FOR ANY ABNORMAL ALARM/FAULT. REFER TO DETAILED 365 DAYS TASK LIST. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 720 | DAY(S)
CONTROL PANEL, FIRE ALARM | TO MONITOR AND CONTROL THE LOGIC OPERATING SEQUENCES AND FLOW OF POWER FOR THE FIRE AND ALARM EQUIPMENT OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF THE GENERAL CONTROL PANEL {EQUIPMENT TAG NUMBER} MAY LEAD TO NO SIGNAL TO / FROM FIRE AND GAS DETECTION SYSTEM. AS A RESULT, IT MAY LEAD TO PROCESS/PERSONAL AT RISK. AND AS A RESULT OF SPURIOUS OPERATION TOTAL FAILURE OF ELECTRICAL EQUIPMENT MAY OCCUR. | MALFUNCTIONING OF INPUT SENSING DEVICES & COMMUNICATION | INPUT SENSING DEVICES | 2 | F | RISK RANK 4 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | 188.1137 | 1.8 | IEEE GOLD BOOK PAGE NO. 236 | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | EXAMINE EQUIPMENT FOR DAMAGE, CORROSION AND CONTAMINATION. INSPECT I/O CARDS ARE INTACT AND WORKING PROPERLY. CHECK DISPLAY FOR ANY ABNORMAL ALARM/FAULT. REFER TO DETAILED 365 DAYS TASK LIST. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 720 | DAY(S)
CONTROL PANEL, FIRE ALARM | TO MONITOR AND CONTROL THE LOGIC OPERATING SEQUENCES AND FLOW OF POWER FOR THE FIRE AND ALARM EQUIPMENT OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF STRUCTURAL DEFICIENCY. | STRUCTURAL DEFICIENCY | DEGRADED | STD | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | CABLE INSULATION/GLAND DAMAGED, INDICATION LAMP FAULTY/FUSED, PUSH BUTTON FAULTY MAY CAUSE THE UNDESIRED {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} OPERATION. AS A RESULT, IT MAKES THE FIRE AND GAS DETECTION SYSTEM VULNERABLE TO FAULT. STRUCTURAL DEFICIENCY OF CONTROL PANEL MAY LEAD TO THE PARTIAL FAILURE OF THE EQUIPMENT. | CABLE INSULATION/GLAND DAMAGED, INDICATION LAMP FAULTY/FUSED, PUSH BUTTON FAULTY | CABLE GLAND, INDICATION LAMP, PUSH BUTTON | 2 | D | RISK RANK 4 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | 188.1137 | 1.8 | IEEE GOLD BOOK PAGE NO. 236 | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | INSPECT THE MOUNTING COMPONENTS FOR SECURITY AND REPLACE THE FAULTY COMPONENTS TO MITIGATE THE PROBLEM. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
JUNCTION BOX, FIRE & GAS | TO PROTECT THE CONNECTIONS AND PROVIDE A SAFETY BARRIER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF OVERHEATING. | OVERHEATING | DEGRADED | OHE | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | OVERHEATING/SPARKING IN THE JUNCTION BOX {EQUIPMENT TAG NUMBER} MAY LEAD TO WIRING BURNOUT AND EQUIPMENT AT RISK. CONSEQUENTLY, IT WILL CAUSE POWER OUTAGE TO ASSOCIATED EQUIPMENT AND IT MAY ALSO LEAD THE ELECTRICAL EQUIPMENT TO PARTIAL FAILURE. | LOOSE CONNECTIONS, SHORT CIRCUIT, WATER INVASION, LOOSE/DAMAGED ASSEMBLY, DAMAGED SEAL/GASKET, LOOSE CABLE GLAND, DAMAGED CABLE INSULATION | CABLE LUGS, NUTS AND BOLTS, HOUSING, SEALS AND GASKETS, CABLE GLANDS, TERMINAL STRIPS | 2 | D | RISK RANK 4 | 2 | D | RISK RANK 4 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | CHECK FOR SIGNS OF EXTERNAL CORROSION. INSPECT FOR MOISTURE INSIDE, ACCUMULATION OF DUST/DIRT, WATER INGRESS, SAFE DISTANCE FROM THE SOURCE OF WATER SPLASH/STEAM LEAKAGE. CHECK ALL CONNECTIONS FOR TIGHTNESS. ENSURE THAT DOOR GASKETS/SEALS AND HINGES ARE INTACT. REFER TO DETAILED 365 DAYS TASK LIST. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 365 | DAY(S)
JUNCTION BOX, FIRE & GAS | TO PROTECT THE CONNECTIONS AND PROVIDE A SAFETY BARRIER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | SPURIOUS OPERATION OF THE JUNCTION BOX {EQUIPMENT TAG NUMBER} DUE TO THE FACTORS LIKE DAMAGED ASSEMBLY/HOUSING, DAMAGED SEAL/GASKET, VIBRATION, LOOSE CONNECTIONS, SHORT CIRCUIT, WATER INVASION, LOOSE CABLE GLAND, DAMAGED CABLE INSULATION MAY LEAD TO UNDESIRED OPERATION AND THE POSSIBLE POWER INTERRUPTION. AND AS A RESULT OF SPURIOUS OPERATION TOTAL FAILURE OF ELECTRICAL EQUIPMENT MAY OCCUR. | DAMAGED ASSEMBLY/HOUSING, DAMAGED SEAL/GASKET, VIBRATION, LOOSE CONNECTIONS, SHORT CIRCUIT, WATER INVASION, LOOSE CABLE GLAND, DAMAGED CABLE INSULATION | HOUSING, SEPARATORS, JUNCTION BOX HOUSING, MOUNTING ASSEMBLY, SEALS AND GASKETS, NUTS AND BOLTS, CABLE GLANDS, TERMINAL STRIPS, CABLE LUGS | 3 | D | RISK RANK 3 | 3 | E | RISK RANK 4 | 3 | F | RISK RANK 4 | 3 | F | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENT TO MITIGATE THE PROBLEM. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
JUNCTION BOX, FIRE & GAS | TO PROTECT THE CONNECTIONS AND PROVIDE A SAFETY BARRIER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF STRUCTURAL DEFICIENCY. | STRUCTURAL DEFICIENCY | DEGRADED | STD | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | STRUCTURAL DEFICIENCY OF THE JUNCTION BOX {EQUIPMENT TAG NUMBER} DUE TO THE FACTORS LIKE MOUNTING BOLTS, CABLE GLANDS DAMAGED, MOUNTING BOLTS AND DETERIORATED ASSEMBLY MAY LEAD TO THE POSSIBLE POWER INTERRUPTION. STRUCTURAL DEFICIENCY OF JUNCTION BOX MAY LEAD TO THE PARTIAL FAILURE OF THE EQUIPMENT. | DAMAGED ASSEMBLY/HOUSING, DAMAGED SEAL/GASKET, DAMAGED CABLE GLAND, MOUNTING BOLTS | MOUNTING NUTS AND BOLTS, HOUSING, SEALS AND GASKETS CABLE GLANDS, JUNCTION BOX HOUSING | 2 | D | RISK RANK 4 | 2 | D | RISK RANK 4 | 2 | D | RISK RANK 4 | 2 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENT TO MITIGATE THE PROBLEM. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
JUNCTION BOX, INSTRUMENTATION | TO PROTECT THE CONNECTIONS AND PROVIDE A SAFETY BARRIER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF OVERHEATING. | OVERHEATING | DEGRADED | OHE | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | OVERHEATING/SPARKING IN THE JUNCTION BOX {EQUIPMENT TAG NUMBER} MAY LEAD TO WIRING BURNOUT AND EQUIPMENT AT RISK. CONSEQUENTLY, IT WILL CAUSE POWER OUTAGE TO ASSOCIATED EQUIPMENT AND IT MAY ALSO LEAD THE ELECTRICAL EQUIPMENT TO PARTIAL FAILURE. | LOOSE CONNECTIONS, SHORT CIRCUIT, WATER INVASION, LOOSE/DAMAGED ASSEMBLY, DAMAGED SEAL/GASKET, LOOSE CABLE GLAND, DAMAGED CABLE INSULATION | CABLE LUGS, NUTS AND BOLTS, HOUSING, SEALS AND GASKETS, CABLE GLANDS, TERMINAL STRIPS | 4 | F | RISK RANK 4 | 2 | D | RISK RANK 4 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | RISK RANK 4 | RISK RANK 4 (ACCEPTABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | CHECK FOR SIGNS OF EXTERNAL CORROSION. INSPECT FOR MOISTURE INSIDE, ACCUMULATION OF DUST/DIRT, WATER INGRESS, SAFE DISTANCE FROM THE SOURCE OF WATER SPLASH/STEAM LEAKAGE. CHECK ALL CONNECTIONS FOR TIGHTNESS. ENSURE THAT DOOR GASKETS/SEALS AND HINGES ARE INTACT. REFER TO DETAILED 365 DAYS TASK LIST. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 365 | DAY(S)
JUNCTION BOX, INSTRUMENTATION | TO PROTECT THE CONNECTIONS AND PROVIDE A SAFETY BARRIER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | SPURIOUS OPERATION OF THE JUNCTION BOX {EQUIPMENT TAG NUMBER} DUE TO THE FACTORS LIKE DAMAGED ASSEMBLY/HOUSING, DAMAGED SEAL/GASKET, VIBRATION, LOOSE CONNECTIONS, SHORT CIRCUIT, WATER INVASION, LOOSE CABLE GLAND, DAMAGED CABLE INSULATION MAY LEAD TO UNDESIRED OPERATION AND THE POSSIBLE POWER INTERRUPTION. AND AS A RESULT OF SPURIOUS OPERATION TOTAL FAILURE OF ELECTRICAL EQUIPMENT MAY OCCUR. | DAMAGED ASSEMBLY/HOUSING, DAMAGED SEAL/GASKET, VIBRATION, LOOSE CONNECTIONS, SHORT CIRCUIT, WATER INVASION, LOOSE CABLE GLAND, DAMAGED CABLE INSULATION | HOUSING, SEPARATORS, JUNCTION BOX HOUSING, MOUNTING ASSEMBLY, SEALS AND GASKETS, NUTS AND BOLTS, CABLE GLANDS, TERMINAL STRIPS, CABLE LUGS | 4 | F | RISK RANK 4 | 3 | E | RISK RANK 4 | 3 | F | RISK RANK 4 | 3 | F | RISK RANK 4 | RISK RANK 4 | RISK RANK 4 (ACCEPTABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENT TO MITIGATE THE PROBLEM. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
JUNCTION BOX, INSTRUMENTATION | TO PROTECT THE CONNECTIONS AND PROVIDE A SAFETY BARRIER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF STRUCTURAL DEFICIENCY. | STRUCTURAL DEFICIENCY | DEGRADED | STD | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | STRUCTURAL DEFICIENCY OF THE JUNCTION BOX {EQUIPMENT TAG NUMBER} DUE TO THE FACTORS LIKE MOUNTING BOLTS, CABLE GLANDS DAMAGED, MOUNTING BOLTS AND DETERIORATED ASSEMBLY MAY LEAD TO THE POSSIBLE POWER INTERRUPTION. STRUCTURAL DEFICIENCY OF JUNCTION BOX MAY LEAD TO THE PARTIAL FAILURE OF THE EQUIPMENT. | DAMAGED ASSEMBLY/HOUSING, DAMAGED SEAL/GASKET, DAMAGED CABLE GLAND, MOUNTING BOLTS | MOUNTING NUTS AND BOLTS, HOUSING, SEALS AND GASKETS CABLE GLANDS, JUNCTION BOX HOUSING | 4 | F | RISK RANK 4 | 2 | D | RISK RANK 4 | 2 | D | RISK RANK 4 | 2 | E | RISK RANK 4 | RISK RANK 4 | RISK RANK 4 (ACCEPTABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENT TO MITIGATE THE PROBLEM. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
JUNCTION BOX, INSTRUMENT | TO PROTECT THE CONNECTIONS AND PROVIDE A SAFETY BARRIER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF OVERHEATING. | OVERHEATING | DEGRADED | OHE | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | OVERHEATING/SPARKING IN THE JUNCTION BOX (CPSF-20-JB-001) MAY LEAD TO WIRING BURNOUT AND EQUIPMENT AT RISK. CONSEQUENTLY, IT WILL CAUSE POWER OUTAGE TO ASSOCIATED EQUIPMENT AND IT MAY ALSO LEAD THE ELECTRICAL EQUIPMENT TO PARTIAL FAILURE. | LOOSE CONNECTIONS, SHORT CIRCUIT, WATER INVASION, LOOSE/DAMAGED ASSEMBLY, DAMAGED SEAL/GASKET, LOOSE CABLE GLAND, DAMAGED CABLE INSULATION | CABLE LUGS, NUTS AND BOLTS, HOUSING, SEALS AND GASKETS, CABLE GLANDS, TERMINAL STRIPS | 4 | F | RISK RANK 4 | 2 | D | RISK RANK 4 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | RISK RANK 4 | RISK RANK 4 (ACCEPTABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | CHECK FOR SIGNS OF EXTERNAL CORROSION. INSPECT FOR MOISTURE INSIDE, ACCUMULATION OF DUST/DIRT, WATER INGRESS, SAFE DISTANCE FROM THE SOURCE OF WATER SPLASH/STEAM LEAKAGE. CHECK ALL CONNECTIONS FOR TIGHTNESS. ENSURE THAT DOOR GASKETS/SEALS AND HINGES ARE INTACT. REFER TO DETAILED 365 DAYS TASK LIST. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 365 | DAY(S)
JUNCTION BOX, INSTRUMENT | TO PROTECT THE CONNECTIONS AND PROVIDE A SAFETY BARRIER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | SPURIOUS OPERATION OF THE JUNCTION BOX {EQUIPMENT TAG NUMBER} MAY LEAD TO UNDESIRED OPERATION AND THE POSSIBLE POWER INTERRUPTION. AS A RESULT OF SPURIOUS OPERATION TOTAL FAILURE OF ELECTRICAL EQUIPMENT MAY OCCUR. | DAMAGED ASSEMBLY/HOUSING, DAMAGED SEAL/GASKET, VIBRATION, LOOSE CONNECTIONS, SHORT CIRCUIT, WATER INVASION, LOOSE CABLE GLAND, DAMAGED CABLE INSULATION | HOUSING, SEPARATORS, JUNCTION BOX HOUSING, MOUNTING ASSEMBLY, SEALS AND GASKETS, NUTS AND BOLTS, CABLE GLANDS, TERMINAL STRIPS, CABLE LUGS | 4 | F | RISK RANK 4 | 3 | E | RISK RANK 4 | 3 | F | RISK RANK 4 | 3 | F | RISK RANK 4 | RISK RANK 4 | RISK RANK 4 (ACCEPTABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENT TO MITIGATE THE PROBLEM. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
JUNCTION BOX, INSTRUMENT | TO PROTECT THE CONNECTIONS AND PROVIDE A SAFETY BARRIER FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF STRUCTURAL DEFICIENCY. | STRUCTURAL DEFICIENCY | DEGRADED | STD | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | STRUCTURAL DEFICIENCY OF THE JUNCTION BOX {EQUIPMENT TAG NUMBER} MAY LEAD TO THE POSSIBLE POWER INTERRUPTION AND AS A RESULT IT MAY LEAD TO THE PARTIAL FAILURE OF THE EQUIPMENT. | DAMAGED ASSEMBLY/HOUSING, DAMAGED SEAL/GASKET, DAMAGED CABLE GLAND, MOUNTING BOLTS | MOUNTING NUTS AND BOLTS, HOUSING, SEALS AND GASKETS CABLE GLANDS, JUNCTION BOX HOUSING | 4 | F | RISK RANK 4 | 2 | D | RISK RANK 4 | 2 | D | RISK RANK 4 | 2 | E | RISK RANK 4 | RISK RANK 4 | RISK RANK 4 (ACCEPTABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENT TO MITIGATE THE PROBLEM. | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
TRANSMITTER, LEVEL | TO PROVIDE CONTINUOUS LEVEL MEASUREMENT FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE WILL HAPPEN IN CASE OF ABNORMAL OUTPUT-LOW. | ABNORMAL OUTPUT-LOW | CRITICAL | AOL | AGE-RELATED | EVIDENT | PROCESS AND OPERATIONAL | ABNORMAL OUTPUT-LOW OF LEVEL TRANSMITTER {EQUIPMENT TAG NUMBER} WILL GIVE IMPROPER/FALSE INFORMATION REGARDING {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WHICH MAY CAUSE THE OPERATIONAL EFFECT. | OUT OF ADJUSTMENT | SENSING ELEMENT | 5 | F | RISK RANK 3 | 5 | E | RISK RANK 3 | 5 | E | RISK RANK 3 | 5 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.06 | 1.27 | 6.02 | 89.8819 | 4 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 463 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND CALIBRATION | VISUALLY INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ANY DUST, MOISTURE INSIDE TERMINAL HOUSING. PERFORM TERMINAL TIGHTENING. INSPECT THE IS BARRIER(IF PRESENT IN LOOP) FOR ANY ABNORMALITY. CHECK THE FUNCTIONING OF TRANSMITTER. PERFORM CALIBRATION, IF TRANSMITTER IS PROVIDING ABNORMAL OUTPUT. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 24 | MONTH(S)
TRANSMITTER, LEVEL | TO PROVIDE CONTINUOUS LEVEL MEASUREMENT FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF LEVEL TRANSMITTER {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WILL NOT GIVE INDICATION / VALUE OF TEMPERATURE TO CONTROLLER WHICH MAY RESULT IN UNSTABLE OPERATION AND CONSEQUENTLY PROCESS WILL BE DISTURBED. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | E | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.06 | 1.27 | 6.02 | 89.8819 | 2 | 3.32 | 7.61 | 15.02 | 15 | 2.3 | 463 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK IS BARRIER HEALTHINESS (IF INSTALLED). CHECK FOR ANY DUST, MOISTURE INSIDE TERMINAL HOUSING. PERFORM TERMINAL TIGHTENING. INSPECT THE IS BARRIER(IF PRESENT IN LOOP) FOR ANY ABNORMALITY. PERFORM THE COMBINED VERIFICATION OF TEMPERATURE TRANSMITTER AND SENSOR ASSEMBLY. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
TRANSMITTER, LEVEL | TO PROVIDE CONTINUOUS LEVEL MEASUREMENT FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS IN LEVEL TRANSMITTER {EQUIPMENT TAG NUMBER} CAN CAUSE DISTURBANCE IN MEASURING DESIRED VALUE / OUTPUT OF TEMPERATURE RESULTING IN UNSTABLE OPERATION. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 5 | F | RISK RANK 3 | 5 | E | RISK RANK 3 | 5 | E | RISK RANK 3 | 5 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.06 | 1.27 | 6.02 | 89.8819 | 3 | 3.32 | 7.61 | 15.02 | 15 | 2.3 | 463 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ANY DUST, MOISTURE INSIDE TERMINAL HOUSING. PERFORM TERMINAL TIGHTENING. IF TRANSMITTER DOES NOT RESPOND PROPERLY, PERFORM CALIBRATION ALONG WITH THE TRANSMITTER ASSEMBLY AS PER PROCEDURE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 24 | MONTH(S)
TRANSMITTER, LEVEL | TO PROVIDE CONTINUOUS LEVEL MEASUREMENT FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF LEVEL TRANSMITTER {EQUIPMENT TAG NUMBER} WILL RESULT IN IMPROPER TEMPERATURE INFORMATION RESULTING IN UNSTABLE OPERATION OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | BLOCKAGE/PLUGGED, FAULTY SIGNAL/INDICATION/ALARM, INSTRUMENT FAILURE-GENERAL, NO SIGNAL/INDICATION/ALARM | ELECTRONICS (CONDITIONING), SENSING ELEMENT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.45 | 2.54 | 7.99 | 44.9409 | 1.5 | 3.32 | 7.61 | 15.02 | 15 | 2.3 | 463 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND CALIBRATION | INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. PERFORM TERMINALS TIGHTENING OF TRANSMITTER. CHECK FOR ADEQUATE VOLTAGE TO THE TRANSMITTER. VISUALLY CHECK FOR LCD DISPLAY FOR ABNORMALITY ETC. CHECK THE ALARMS AND DIAGNOSTIC MESSAGES. IF TRANSMITTER DOES NOT RESPOND PROPERLY, PERFORM CALIBRATION ALONG WITH THE TRANSMITTER ASSEMBLY AS PER PROCEDURE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 24 | MONTH(S)
TRANSMITTER, VIBRATION | TO PROVIDE INFORMATION ABOUT VIBRATION ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF ABNORMAL OUTPUT-LOW. | ABNORMAL OUTPUT-LOW | CRITICAL | AOL | AGE-RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | ABNORMAL OUTPUT-LOW OF VIBRATION TRANSMITTER {EQUIPMENT TAG NUMBER} ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL LEAD TO GIVE FALSE INFORMATION OF VIBRATION RESULTING IN EQUIPMENT FAILURE AND SAFETY RISK. | OUT OF ADJUSTMENT | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.29 | 1.4 | 393.4205 | 4 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND CALIBRATION | VISUALLY INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ADEQUATE VOLTAGES. INSPECT FOR INTERMITTENT SHORTS. CHECK FOR LCD DISPLAY ABNORMALITY. IF ANY ABNORMALITY FOUND, PERFORM CALIBRATION. CHECK FOR ANY WATER INGRESS INSIDE THE HOUSING. CARRY OUT CALIBRATION OF TRANSMITTER. | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
TRANSMITTER, VIBRATION | TO PROVIDE INFORMATION ABOUT VIBRATION ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE WILL OCCURE IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | FAIL TO FUNCTION ON DEMAND OF VIBRATION TRANSMITTER {EQUIPMENT TAG NUMBER} ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL LEAD TO GIVE FALSE INFORMATION OF VIBRATION RESULTING IN EQUIPMENT FAILURE AND SAFETY RISK. | BLOCKAGE/PLUGGED, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM, ELECTRICAL FAILURE GENERAL, INSTRUMENT FAILURE GENERAL | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION, CALIBRATION AND FUNCTIONAL TEST | VISUALLY INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ANY DUST, MOISTURE INSIDE TERMINAL HOUSING. CHECK IF ADEQUATE VOLTAGE SUPPLY IS AVAILABLE FOR THE TRANSMITTER PERFORM TERMINAL TIGHTENING. PERFORM THE COMBINED VERIFICATION OF TRANSMITTER AND SENSOR ASSEMBLY. PERFORM FUNCTION TEST OF THE TRANSMITTER | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
TRANSMITTER, VIBRATION | TO PROVIDE INFORMATION ABOUT VIBRATION ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS OF VIBRATION TRANSMITTER {EQUIPMENT TAG NUMBER} ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL LEAD TO GIVE FALSE INFORMATION OF VIBRATION RESULTING IN EQUIPMENT FAILURE AND SAFETY RISK. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | 4 | F | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION, CALIBRATION AND FUNCTIONAL TEST | VISUALLY INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. CHECK FOR ANY DUST, MOISTURE INSIDE TERMINAL HOUSING. PERFORM TERMINAL TIGHTENING. CHECK THE ALARMS AND DIAGNOSTIC MESSAGES. IF TRANSMITTER DOES NOT RESPOND PROPERLY, PERFORM CALIBRATION ALONG WITH THE ELEMENT ASSEMBLY AS PER PROCEDURE. | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
TRANSMITTER, VIBRATION | TO PROVIDE INFORMATION ABOUT VIBRATION ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE WILL OCCURE IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF VIBRATION TRANSMITTER {EQUIPMENT TAG NUMBER} ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL LEAD TO GIVE FALSE INFORMATION OF VIBRATION RESULTING IN EQUIPMENT FAILURE AND SAFETY RISK. | BLOCKAGE/PLUGGED, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM, INSTRUMENT FAILURE GENERAL | ELECTRONICS (CONDITIONING), SENSING ELEMENT | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.58 | 1.47 | 3.09 | 77.6531 | 2.2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND CALIBRATION | INSPECT THE TRANSMITTER FOR MECHANICAL AND ELECTRICAL INTEGRITY AND SECURITY OF ATTACHMENTS. PERFORM TERMINALS TIGHTENING OF TRANSMITTER. CHECK FOR ADEQUATE VOLTAGE TO THE TRANSMITTER. VISUALLY CHECK FOR LCD DISPLAY FOR ABNORMALITY ETC. CHECK THE ALARMS AND DIAGNOSTIC MESSAGES. IF TRANSMITTER DOES NOT RESPOND PROPERLY, PERFORM CALIBRATION ALONG WITH THE TRANSMITTER ASSEMBLY AS PER PROCEDURE. | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
ELEMENT, BURNER | TO PROVIDE THE FIRE AND BURN THE FLUE GASSES AT {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF EXTERNAL LEAKAGE-FUEL. | EXTERNAL LEAKAGE-FUEL | DEGRADED | ELF | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | EXCESSIVE LEAKAGE OF {SERVICE} WILL AFFECT THE PERFORMANCE OF BURNER ELEMENT {EQUIPMENT TAG NUMBER} AND ALSO SAFETY AND ENVIRONMENT. | LEAKAGE, MISCELLANEOUS-GENERAL | SEALS | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | INSPECT ELECTRICAL COMPONENTS FOR ANY ABNORMALITY AND SIGN OF BURNS. CHECK CONTROL UNIT FOR PROPER FUNCTIONING CHECK SPARK PLUGS FOR CLEANING AND REPLACEMENT CHECK BURNERS FOR CLEANING AND REPLACEMENT | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
ELEMENT, BURNER | TO PROVIDE THE FIRE AND BURN THE FLUE GASSES AT {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF STRUCTURAL DEFICIENCY. | STRUCTURAL DEFICIENCY | DEGRADED | STD | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | STRUCTURAL DEFICIENCY OF BURNER ELEMENT {EQUIPMENT TAG NUMBER} WILL CAUSE AIR AND FUEL MIXTURE TO NOT BURN PROPERLY WHICH WILL LEAD TO INEFFICIENCY OF BURNER. | CORROSION, DEFORMATION, WEAR, MATERIAL FAILURE- GENERAL | NOZZLE, FLANGE, PIPING, VALVES | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | INSPECT ELECTRICAL COMPONENTS FOR ANY ABNORMALITY AND SIGN OF BURNS. CHECK CONTROL UNIT FOR PROPER FUNCTIONING CHECK SPARK PLUGS FOR CLEANING AND REPLACEMENT CHECK BURNERS FOR CLEANING AND REPLACEMENT | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
ELEMENT, BURNER | TO PROVIDE THE FIRE AND BURN THE FLUE GASSES AT {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF LOW OUTPUT. | LOW OUTPUT | DEGRADED | LOO | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | LOW OUTPUT WILL AFFECT THE PERFORMANCE OF BURNER ELEMENT {EQUIPMENT TAG NUMBER} AND WILL RESULT IN LESS FIRE AND LOW BURNING OF THE FLUE GASSES AT FLARE TIP. | ELECTRICAL FAILURE, DEGRADED SPARK PLUGS, CLOGGED BURNERS | ELECTRICAL CONNECTIONS, CONTROL UNIT, SPARK PLUGS | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | INSPECT ELECTRICAL COMPONENTS FOR ANY ABNORMALITY AND SIGN OF BURNS. CHECK CONTROL UNIT FOR PROPER FUNCTIONING CHECK SPARK PLUGS FOR CLEANING AND REPLACEMENT CHECK BURNERS FOR CLEANING AND REPLACEMENT | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
BURNER, ELEMENT | TO PROVIDE THE FIRE AND BURN THE FLUE GASSES AT {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF EXTERNAL LEAKAGE-FUEL. | EXTERNAL LEAKAGE-FUEL | DEGRADED | ELF | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | EXCESSIVE LEAKAGE OF FUEL WILL AFFECT THE PERFORMANCE OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} AND ALSO SAFETY AND ENVIRONMENT. | LEAKAGE, MISCELLANEOUS-GENERAL | SEALS | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND EMISSION TEST | BURNER INSPECTION AND CLEANING. CO/NOX EMISSIONS TESTING. COMBUSTION CONTROL SYSTEM FUNCTION TEST. INSPECT SIGNS OF CORROSION, DAMAGE AND LEAKS. CHECK AND CLEAN THE SPARK PLUGS. CHECK AND CLEAN THE BURNER ELEMENT. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
BURNER, ELEMENT | TO PROVIDE THE FIRE AND BURN THE FLUE GASSES AT {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF STRUCTURAL DEFICIENCY. | STRUCTURAL DEFICIENCY | DEGRADED | STD | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | STRUCTURAL DEFICIENCY OF BURNER {EQUIPMENT TAG NUMBER} WILL CAUSE AIR AND FUEL MIXTURE TO NOT BURN PROPERLY WHICH WILL LEAD TO INEFFICIENCY OF BURNER. | CORROSION, DEFORMATION, WEAR, MATERIAL FAILURE- GENERAL | NOZZLE, FLANGE, PIPING, VALVES | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND EMISSION TEST | BURNER INSPECTION AND CLEANING. CO/NOX EMISSIONS TESTING. COMBUSTION CONTROL SYSTEM FUNCTION TEST. INSPECT SIGNS OF CORROSION, DAMAGE AND LEAKS. CHECK AND CLEAN THE SPARK PLUGS. CHECK AND CLEAN THE BURNER ELEMENT. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
BURNER, ELEMENT | TO PROVIDE THE FIRE AND BURN THE FLUE GASSES AT {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF LOW OUTPUT. | LOW OUTPUT | DEGRADED | LOO | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | LOW OUTPUT WILL AFFECT THE PERFORMANCE OF BURNER {EQUIPMENT TAG NUMBER} AND WILL RESULT IN LESS FIRE AND LOW BURNING OF THE FLUE GASSES AT {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | ELECTRICAL FAILURE, DEGRADED SPARK PLUGS, CLOGGED BURNERS | ELECTRICAL CONNECTIONS, CONTROL UNIT, SPARK PLUGS | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND EMISSION TEST | BURNER INSPECTION AND CLEANING. CO/NOX EMISSIONS TESTING. COMBUSTION CONTROL SYSTEM FUNCTION TEST. INSPECT SIGNS OF CORROSION, DAMAGE AND LEAKS. CHECK AND CLEAN THE SPARK PLUGS. CHECK AND CLEAN THE BURNER ELEMENT. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
FIRE HYDRANT | TO PROVIDE THE {SERVICE} FOR EXTINGUISHING/CONTROLLING THE FIRE. | TOTAL FAILURE OF FUNCTION WILL OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | FAIL TO FUNCTION ON DEMAND OF FIRE HYDRANT {EQUIPMENT TAG NUMBER} WILL LEAD TO SAFETY HAZARD. | CORROSION, BLOCKAGE, PAINT HAS LOCKED OPERATING NUT TO BONNET, HYDRANT OR SUPPLY VALE IS NOT FULLY OPEN | SUPPLY VALVE, FASTENERS, NOZZLE | 5 | C | RISK RANK 1 | 5 | C | RISK RANK 1 | 5 | D | RISK RANK 2 | 5 | D | RISK RANK 2 | RISK RANK 1 | RISK RANK 1 (INTOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | INSPECTION AND FUNCTION TEST: CONDUCT A FUNCTION TEST TO ENSURE THAT ALL THE COMPONENTS PERFORM THEIR ORIGINAL DESIGN EXPECTATIONS. | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 1 | YEAR(S)
FIRE HYDRANT | TO PROVIDE THE {SERVICE} FOR EXTINGUISHING/CONTROLLING THE FIRE. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN AND MAY LEAD TO TOTAL FAILURE. | MINOR IN-SERVICE PROBLEMS | DEGRADED | SER | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | MINOR IN-SERVICE PROBLEMS MAY CAUSE DEGRADED OPERATION OF FIRE HYDRANT {EQUIPMENT TAG NUMBER} AND CAUSE OF SAFETY RISK IN EMERGENCY CONDITION. | HYDRANT OR SUPPLY VALE IS NOT FULLY OPEN, LOOSENESS | SUPPLY VALVE, FASTENERS, O-RINGS, GASKET, FASTENERS | 5 | C | RISK RANK 1 | 5 | C | RISK RANK 1 | 5 | D | RISK RANK 2 | 5 | D | RISK RANK 2 | RISK RANK 1 | RISK RANK 1 (INTOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | INSPECTION AND FUNCTION TEST: CHECK THE HYDRANT FOR MECHANICAL DAMAGE, LEAKS AND GENERAL CONDITION. CONDUCT A FUNCTION TEST TO ENSURE THAT ALL THE COMPONENTS PERFORM THEIR ORIGINAL DESIGN EXPECTATIONS. LUBRICATE THE HYDRANT TO ENSURE THAT ALL STEMS, CAPS, PLUGS, AND THREADS ARE IN PROPER OPERATING CONDITION. | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 1 | YEAR(S)
FIRE HYDRANT | TO PROVIDE THE {SERVICE} FOR EXTINGUISHING/CONTROLLING THE FIRE. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN AND MAY LEAD TO TOTAL FAILURE. | EXTERNAL LEAKAGE-UTILITY MEDIUM | DEGRADED | ELU | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | EXTERNAL LEAKAGE FROM FIRE HYDRANT {EQUIPMENT TAG NUMBER} CAUSE THE LOSS OF VALUABLE FIRE WATER WHICH CAN BE USED IN EMERGENCY AS WELL AS DROP OF PRESSURE RESULTING IN FAILURE OF ACHIEVING THE REQUIRED PRESSURE WHEN NEEDED. | BREAKAGE, CORROSION, DAMAGED VALVE DISC OR NOZZLE SEALING SURFACE, DAMAGED STEM O-RINGS | VALVE DISC, STEM O-RINGS, GASKET, FASTENERS | 5 | C | RISK RANK 1 | 5 | C | RISK RANK 1 | 5 | D | RISK RANK 2 | 5 | D | RISK RANK 2 | RISK RANK 1 | RISK RANK 1 (INTOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | INSPECTION AND FUNCTION TEST: CHECK THE HYDRANT FOR MECHANICAL DAMAGE, LEAKS AND GENERAL CONDITION. CONDUCT A FUNCTION TEST TO ENSURE THAT ALL THE COMPONENTS PERFORM THEIR ORIGINAL DESIGN EXPECTATIONS. | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 1 | YEAR(S)
MONITOR, FIRE WATER/FOAM | TO PROVIDE THE {SERVICE} FOR EXTINGUISHING/CONTROLLING THE FIRE. | TOTAL FAILURE OF FUNCTION WILL OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | FAIL TO FUNCTION ON DEMAND OF FIRE WATER/FOAM MONITOR {EQUIPMENT TAG NUMBER} WILL LEAD TO SAFETY HAZARD. | CORROSION, BLOCKAGE, PAINT HAS LOCKED OPERATING NUT TO BONNET, HYDRANT OR SUPPLY VALE IS NOT FULLY OPEN | SUPPLY VALVE, FASTENERS, NOZZLE | 5 | C | RISK RANK 1 | 5 | C | RISK RANK 1 | 5 | D | RISK RANK 2 | 5 | D | RISK RANK 2 | RISK RANK 1 | RISK RANK 1 (INTOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | INSPECTION AND FUNCTION TEST: CONDUCT A FUNCTION TEST TO ENSURE THAT ALL THE COMPONENTS PERFORM THEIR ORIGINAL DESIGN EXPECTATIONS. | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 1 | YEAR(S)
MONITOR, FIRE WATER/FOAM | TO PROVIDE THE {SERVICE} FOR EXTINGUISHING/CONTROLLING THE FIRE. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN AND MAY LEAD TO TOTAL FAILURE. | MINOR IN-SERVICE PROBLEMS | DEGRADED | SER | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | MINOR IN-SERVICE PROBLEMS MAY CAUSE DEGRADED OPERATION OF FIRE WATER/FOAM MONITOR {EQUIPMENT TAG NUMBER} AND CAUSE OF SAFETY RISK IN EMERGENCY CONDITION. | HYDRANT OR SUPPLY VALE IS NOT FULLY OPEN, LOOSENESS | SUPPLY VALVE, FASTENERS, O-RINGS, GASKET, FASTENERS | 5 | C | RISK RANK 1 | 5 | C | RISK RANK 1 | 5 | D | RISK RANK 2 | 5 | D | RISK RANK 2 | RISK RANK 1 | RISK RANK 1 (INTOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION | INSPECTION: INSPECT THE MONITOR OR NOZZLES FOR PHYSICAL DAMAGE, LEAKAGE AND CORROSION. | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 1 | YEAR(S)
MONITOR, FIRE WATER/FOAM | TO PROVIDE THE {SERVICE} FOR EXTINGUISHING/CONTROLLING THE FIRE. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN AND MAY LEAD TO TOTAL FAILURE. | EXTERNAL LEAKAGE-UTILITY MEDIUM | DEGRADED | ELU | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | EXTERNAL LEAKAGE FROM FIRE WATER/FOAM MONITOR {EQUIPMENT TAG NUMBER} CAUSE THE LOSS OF VALUABLE {SERVICE} WHICH CAN BE USED IN EMERGENCY AS WELL AS DROP OF PRESSURE RESULTING IN FAILURE OF ACHIEVING THE REQUIRED PRESSURE WHEN NEEDED. | BREAKAGE, CORROSION, DAMAGED VALVE DISC OR NOZZLE SEALING SURFACE, DAMAGED STEM O-RINGS | VALVE DISC, STEM O-RINGS, GASKET, FASTENERS | 5 | C | RISK RANK 1 | 5 | C | RISK RANK 1 | 5 | D | RISK RANK 2 | 5 | D | RISK RANK 2 | RISK RANK 1 | RISK RANK 1 (INTOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | INSPECTION AND FUNCTION TEST: CHECK THE HYDRANT MONITOR FOR MECHANICAL DAMAGE, LEAKS AND GENERAL CONDITION. CONDUCT A FUNCTION TEST TO ENSURE THAT ALL THE COMPONENTS PERFORM THEIR ORIGINAL DESIGN EXPECTATIONS. | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 1 | YEAR(S)
RECORDER, FLOW | TO RECORD THE FLOW RATE FOR OUTLET OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF FLOW RECORDER {EQUIPMENT TAG NUMBER} MOUNTED ON{PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, IT WOULD NOT RECORD INFORMATON ABOUT PROCESS, THIS MAY LEAD TO PROCESS DISTURBANCE AND THE PRODUCTION LOSS. | BLOCKAGE/PLUGGED, ELECTRICAL FAILURE-GENERAL, INSTRUMENT FAILURE-GENERAL, FAULTY SIGNAL/INDICATION/ALARM, NO SIGNAL/INDICATION/ALARM | ELECTRONIC (CONDITIONING), SENSING ELEMENT, SUBUNIT | 5 | E | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | 5 | F | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.77 | 1.76 | 3.48 | 64.858 | 3.3 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | ISOLATE THE FLOW METER FROM THE PROCESS MEDIUM AND DEPRESSURIZE THROUGH THE VENT/DRAIN POINT, PRIOR TO CARRYING OUT ANY WORK. CLEAN THE V-CONE OR WASH ALL PARTS WITH PROCESS COMPATIBLE SOLVENT TO REMOVE ANY DIRT. (FOR MORE DETAILS, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 18 | MONTH(S)
RECORDER, FLOW | TO RECORD THE FLOW RATE FOR OUTLET OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF MINOR IN-SERVICE PROBLEMS. | MINOR IN-SERVICE PROBLEMS | INCIPIENT | SER | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | MINOR IN-SERVICE PROBLEMS IN FLOW RECORDER {EQUIPMENT TAG NUMBER} MOUNTED ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} WILL CAUSE INACCURATE MEASUREMENT OF FLOW WHICH WILL LEAD TOWARDS PROCESS INTERRUPTION. | FAULTY SIGNAL/INDICATION/ALARM, LEAKAGE | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.24 | 0.88 | 2.28 | 129.7159 | 2 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | ISOLATE THE FLOW METER FROM THE PROCESS MEDIUM AND DEPRESSURIZE THROUGH THE VENT/DRAIN POINT, PRIOR TO CARRYING OUT ANY WORK. CLEAN THE V-CONE OR WASH ALL PARTS WITH PROCESS COMPATIBLE SOLVENT TO REMOVE ANY DIRT. (FOR MORE DETAILS, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 18 | MONTH(S)
RECORDER, FLOW | TO RECORD THE FLOW RATE FOR OUTLET OF {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE WILL HAPPEN IN CASE OF ABNORMAL OUTPUT-LOW. | ABNORMAL OUTPUT-LOW | CRITICAL | AOL | AGE-RELATED | EVIDENT | PROCESS AND OPERATIONAL | ABNORMAL OUTPUT-LOW OF FLOW RECORDER {EQUIPMENT TAG NUMBER} MOUNTED ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} MAY CAUSE INACCURATE INFORMATION ABOUT FLOW RESULTING IN THE PROCESS DISTURBANCE AND THE UNSTABLE OPERATION. | OUT OF ADJUSTMENT | SENSING ELEMENT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.29 | 1.4 | 393.4205 | 4 | 2.95 | 4.71 | 7.15 | 24.2357 | 2.7 | 457 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | ISOLATE THE FLOW METER FROM THE PROCESS MEDIUM AND DEPRESSURIZE THROUGH THE VENT/DRAIN POINT, PRIOR TO CARRYING OUT ANY WORK. CLEAN THE V-CONE OR WASH ALL PARTS WITH PROCESS COMPATIBLE SOLVENT TO REMOVE ANY DIRT. (FOR MORE DETAILS, REFER TO PMR) | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 18 | MONTH(S)
VALVE, REGULATING | TO REGULATE THE PRESSURE SUPPLIED TO A SUB-SYSTEM OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-PROCESS MEDIUM. | EXTERNAL LEAKAGE-PROCESS MEDIUM | DEGRADED | ELP | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | EXTERNAL LEAKAGE OF PRESSURE REGULATING VALVE {EQUIPMENT TAG NUMBER} CAN LEAD TO THE UNWANTED PRESSURE DROP ACROSS THE VALVE, WHICH MAY CAUSE DISTURBANCE IN OPERATION AND ENVIRONMENTAL CONSEQUENCES MAY HAPPEN. | LOOSENESS | STEM | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 2 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENT/ACTION TO MITIGATE THE LEAKAGE. CHECK FOR BOLTS TIGHTNESS. REPLACE CONSUMABLES LIKE GASKETS, O-RINGS ETC. (FOR DETAIL, REFER TO PMR) | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, REGULATING | TO REGULATE THE PRESSURE SUPPLIED TO A SUB-SYSTEM OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-UTILITY MEDIUM. | EXTERNAL LEAKAGE-UTILITY MEDIUM | DEGRADED | ELU | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | EXTERNAL LEAKAGE-UTILITY MEDIUM FROM PRESSURE REGULATING VALVE {EQUIPMENT TAG NUMBER} MOUNTED ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} LINE CAN LEAD TO THE ABRUPT/UNWANTED CHANGE IN THE VALVE STATE AND THUS LIMITING THE VALVE TO PERFORM TASK EFFICIENTLY. | MECHANICAL FAILURE-GENERAL | SUBUNIT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 4 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENTS/ACTION TO MITIGATE THE LEAKAGE. REPLACE CONSUMABLES LIKE GASKETS, O RINGS ETC. (FOR DETAIL, REFER TO PMR) | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, REGULATING | TO REGULATE THE PRESSURE SUPPLIED TO A SUB-SYSTEM OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF PLUGGED/CHOKED. | PLUGGED/CHOKED | DEGRADED | PLU | AGE-RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | IF PRESSURE REGULATING VALVE {EQUIPMENT TAG NUMBER} PLUGGED/CHOKED DUE TO FOREIGN MATERIAL, IT WOULD NOT WORK PROPERLY AND ULTIMATELY IT WILL LEAD TO PROCESS AT RISK. | BLOCKAGE/PLUGGED | CLOSURE MEMBER (BALL/GATE/DISC/ETC.) | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.12 | 0.76 | 1.86 | 150.1973 | - | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | PERFORM MAJOR OVERHAULING OF THE VALVE, SEAT DISC LAPPING, CLEANING AND SERVICING OF VALVE INTERNALS, AND REPLACEMENT OF ALL SEALS/SOFT GOODS. PERFORM LEAK TEST OF THE VALVE AND ENSURE THAT VALVE CONFORMS TO THE DESIGN VALVE LEAKAGE CLASSIFICATION AS SET OUT IN THE VALVE TAG PLATE OR DATASHEET. ENSURE THE CONTROL VALVE COMPONENTS AND ASSOCIATED CABLING ARE IN GOOD CONDITION, SECURELY FITTED AND FIT FOR PURPOSE. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 36 | MONTH(S)
VALVE, REGULATING | TO REGULATE THE PRESSURE SUPPLIED TO A SUB-SYSTEM OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF VALVE LEAKAGE IN CLOSED POSITION. | VALVE LEAKAGE IN CLOSED POSITION | CRITICAL | LCP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF VALVE LEAKAGE IN CLOSED POSITION OF PRESSURE REGULATING VALVE {EQUIPMENT TAG NUMBER} EXCEEDS THAN ACCEPTABLE LEAKAGE RATE, SO IT WOULD NOT BE POSSIBLE TO CONTROL THE PROCESS, WHICH RESULT AS PROCESS DISTURBANCE. | LOOSENESS, CORROSION, INSTRUMENT FAILURE-GENERAL | PACKING, SEAT RINGS, SUBUNIT | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 10 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | PERFORM MAJOR OVERHAULING OF THE VALVE, SEAT DISC LAPPING, CLEANING AND SERVICING OF VALVE INTERNALS, AND REPLACEMENT OF ALL SEALS/SOFT GOODS. PERFORM LEAK TEST OF THE VALVE AND ENSURE THAT VALVE CONFORMS TO THE DESIGN VALVE LEAKAGE CLASSIFICATION AS SET OUT IN THE VALVE TAG PLATE OR DATASHEET. ENSURE THE CONTROL VALVE COMPONENTS AND ASSOCIATED CABLING ARE IN GOOD CONDITION, SECURELY FITTED AND FIT FOR PURPOSE. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 36 | MONTH(S)
VALVE, REGULATING | TO REGULATE THE PRESSURE SUPPLIED TO A SUB-SYSTEM OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO REGULATE. | FAIL TO REGULATE | CRITICAL | FTR | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF PRESSURE REGULATING VALVE {EQUIPMENT TAG NUMBER} FAIL TO REGULATE, IT WOULD NOT BE POSSIBLE TO CONTROL/KEEP THE PROCESS AT A SET POINT, THIS MAY LEADS TO PROCESS DISTURBANCE. | BLOCKAGE/PLUGGED, INSTRUMENT FAILURE-GENERAL | VALVE BODY W/INTERNALS | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.28 | 1.14 | 2.46 | 100.1316 | 2.7 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT FOR ACTUATOR AND ALL THE TUBING CONNECTIONS FOR UTILITY LEAKAGE AND CHECK POSITIONER FEEDBACK LINK FOR LOOSENESS. ENSURE THAT PROPER INSTRUMENT AIR SUPPLY IS PROVIDING TO POSITIONER AND ACTUATOR AS PER DATA SHEET. ENSURE THAT STEM COUPLING (STEM CONNECTOR) OF ACTUATOR AND VALVE BODY IS TIGHTENED AND PROPERLY ADJUSTED. PERFORM LUBRICATION OF VALVE AND GEARBOX(IF PRESENT). CHECK VALVE TRAVEL IS SAME AS VALVE DATA PLATE. IF THE VALVE STEM TRAVEL INDICATION DIDN’T SHOW CORRECTLY 0% OR 100% TRAVEL AND ANY OFFSET FOUND, PERFORM CALIBRATION OF THE VALVE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 12 | MONTH(S)
VALVE, PRESSURE RELIEF | TO RELIEF EXCESSIVE PRESSURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-PROCESS MEDIUM. | EXTERNAL LEAKAGE-PROCESS MEDIUM | DEGRADED | ELP | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | EXTERNAL LEAKAGE OF PRESSURE RELIEF VALVE {EQUIPMENT TAG NUMBER} CAN LEAD TO THE UNWANTED PRESSURE DROP ACROSS THE VALVE, WHICH MAY CAUSE DISTURBANCE IN OPERATION AND ENVIRONMENTAL CONSEQUENCES MAY HAPPEN. | LOOSENESS | STEM | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 2 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENT/ACTION TO MITIGATE THE LEAKAGE. CHECK FOR BOLTS TIGHTNESS. REPLACE CONSUMABLES LIKE GASKETS, O-RINGS ETC. (FOR DETAIL, REFER TO PMR) | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, PRESSURE RELIEF | TO RELIEF EXCESSIVE PRESSURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-UTILITY MEDIUM. | EXTERNAL LEAKAGE-UTILITY MEDIUM | DEGRADED | ELU | NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | EXTERNAL LEAKAGE-UTILITY MEDIUM OF PRESSURE RELIEF VALVE {EQUIPMENT TAG NUMBER} CAN LEAD TO THE UNWANTED PRESSURE DROP ACROSS THE VALVE, WHICH MAY CAUSE DISTURBANCE IN PROCESS AND ITS OPERATION AND ENVIRONMENTAL CONSEQUENCES MAY HAPPEN. | MECHANICAL FAILURE-GENERAL | SUBUNIT | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 4 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENTS/ACTION TO MITIGATE THE LEAKAGE. REPLACE CONSUMABLES LIKE GASKETS, O RINGS ETC. (FOR DETAIL, REFER TO PMR) | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, PRESSURE RELIEF | TO RELIEF EXCESSIVE PRESSURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF PLUGGED/CHOKED. | PLUGGED/CHOKED | DEGRADED | PLU | AGE-RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | IF PRESSURE RELIEF VALVE {EQUIPMENT TAG NUMBER} PLUGGED/CHOKED DUE TO FOREIGN MATERIAL, IT WOULD NOT WORK PROPERLY AND ULTIMATELY IT WILL LEAD TO PROCESS AT RISK. | BLOCKAGE/PLUGGED | CLOSURE MEMBER (BALL/GATE/DISC/ETC.) | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.12 | 0.76 | 1.86 | 150.1973 | - | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | PERFORM MAJOR OVERHAULING OF THE VALVE, SEAT DISC LAPPING, CLEANING AND SERVICING OF VALVE INTERNALS, AND REPLACEMENT OF ALL SEALS/SOFT GOODS. PERFORM LEAK TEST OF THE VALVE AND ENSURE THAT VALVE CONFORMS TO THE DESIGN VALVE LEAKAGE CLASSIFICATION AS SET OUT IN THE VALVE TAG PLATE OR DATASHEET. ENSURE THE CONTROL VALVE COMPONENTS AND ASSOCIATED CABLING ARE IN GOOD CONDITION, SECURELY FITTED AND FIT FOR PURPOSE. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 36 | MONTH(S)
VALVE, PRESSURE RELIEF | TO RELIEF EXCESSIVE PRESSURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF VALVE LEAKAGE IN CLOSED POSITION. | VALVE LEAKAGE IN CLOSED POSITION | CRITICAL | LCP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF VALVE LEAKAGE IN CLOSED POSITION OF PRESSURE RELIEF VALVE {EQUIPMENT TAG NUMBER} EXCEEDS THAN ACCEPTABLE LEAKAGE RATE, SO IT WOULD NOT BE POSSIBLE TO CONTROL THE PROCESS, WHICH RESULT AS PROCESS DISTURBANCE. | LOOSENESS, CORROSION, INSTRUMENT FAILURE-GENERAL | PACKING, SEAT RINGS, SUBUNIT | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 10 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | PERFORM MAJOR OVERHAULING OF THE VALVE, SEAT DISC LAPPING, CLEANING AND SERVICING OF VALVE INTERNALS, AND REPLACEMENT OF ALL SEALS/SOFT GOODS. PERFORM LEAK TEST OF THE VALVE AND ENSURE THAT VALVE CONFORMS TO THE DESIGN VALVE LEAKAGE CLASSIFICATION AS SET OUT IN THE VALVE TAG PLATE OR DATASHEET. ENSURE THE CONTROL VALVE COMPONENTS AND ASSOCIATED CABLING ARE IN GOOD CONDITION, SECURELY FITTED AND FIT FOR PURPOSE. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 36 | MONTH(S)
VALVE, PRESSURE RELIEF | TO RELIEF EXCESSIVE PRESSURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO REGULATE. | FAIL TO REGULATE | CRITICAL | FTR | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF PRESSURE RELIEF VALVE {EQUIPMENT TAG NUMBER} FAIL TO REGULATE, IT WOULD NOT BE POSSIBLE TO CONTROL/KEEP THE PROCESS AT A SET POINT, THIS MAY LEADS TO PROCESS DISTURBANCE. | BLOCKAGE/PLUGGED, INSTRUMENT FAILURE-GENERAL | VALVE BODY W/INTERNALS | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.28 | 1.14 | 2.46 | 100.1316 | 2.7 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT FOR ACTUATOR AND ALL THE TUBING CONNECTIONS FOR UTILITY LEAKAGE AND CHECK POSITIONER FEEDBACK LINK FOR LOOSENESS. ENSURE THAT PROPER INSTRUMENT AIR SUPPLY IS PROVIDING TO POSITIONER AND ACTUATOR AS PER DATA SHEET. ENSURE THAT STEM COUPLING (STEM CONNECTOR) OF ACTUATOR AND VALVE BODY IS TIGHTENED AND PROPERLY ADJUSTED. PERFORM LUBRICATION OF VALVE AND GEARBOX(IF PRESENT). CHECK VALVE TRAVEL IS SAME AS VALVE DATA PLATE. IF THE VALVE STEM TRAVEL INDICATION DIDN’T SHOW CORRECTLY 0% OR 100% TRAVEL AND ANY OFFSET FOUND, PERFORM CALIBRATION OF THE VALVE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 12 | MONTH(S)
VALVE, PRESSURE VACCUM RELIEF | TO RELIEF EXCESSIVE PRESSURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-PROCESS MEDIUM. | EXTERNAL LEAKAGE-PROCESS MEDIUM | DEGRADED | ELP | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | EXTERNAL LEAKAGE OF PRESSURE RELIEF VALVE {EQUIPMENT TAG NUMBER} CAN LEAD TO THE UNWANTED PRESSURE DROP ACROSS THE VALVE, WHICH MAY CAUSE DISTURBANCE IN OPERATION AND ENVIRONMENTAL CONSEQUENCES MAY HAPPEN. | LOOSENESS | STEM | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 2 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENT/ACTION TO MITIGATE THE LEAKAGE. CHECK FOR BOLTS TIGHTNESS. REPLACE CONSUMABLES LIKE GASKETS, O-RINGS ETC. (FOR DETAIL, REFER TO PMR) | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, PRESSURE VACCUM RELIEF | TO RELIEF EXCESSIVE PRESSURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-UTILITY MEDIUM. | EXTERNAL LEAKAGE-UTILITY MEDIUM | DEGRADED | ELU | NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | EXTERNAL LEAKAGE-UTILITY MEDIUM OF PRESSURE VACCUM RELIEF VALVE {EQUIPMENT TAG NUMBER} CAN LEAD TO THE UNWANTED PRESSURE DROP ACROSS THE VALVE, WHICH MAY CAUSE DISTURBANCE IN PROCESS AND ITS OPERATION AND ENVIRONMENTAL CONSEQUENCES MAY HAPPEN. | MECHANICAL FAILURE-GENERAL | SUBUNIT | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 4 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENTS/ACTION TO MITIGATE THE LEAKAGE. REPLACE CONSUMABLES LIKE GASKETS, O RINGS ETC. (FOR DETAIL, REFER TO PMR) | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, PRESSURE VACCUM RELIEF | TO RELIEF EXCESSIVE PRESSURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF PLUGGED/CHOKED. | PLUGGED/CHOKED | DEGRADED | PLU | AGE-RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | IF PRESSURE RELIEF VALVE {EQUIPMENT TAG NUMBER} PLUGGED/CHOKED DUE TO FOREIGN MATERIAL, IT WOULD NOT WORK PROPERLY AND ULTIMATELY IT WILL LEAD TO PROCESS AT RISK. | BLOCKAGE/PLUGGED | CLOSURE MEMBER (BALL/GATE/DISC/ETC.) | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.12 | 0.76 | 1.86 | 150.1973 | - | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | PERFORM MAJOR OVERHAULING OF THE VALVE, SEAT DISC LAPPING, CLEANING AND SERVICING OF VALVE INTERNALS, AND REPLACEMENT OF ALL SEALS/SOFT GOODS. PERFORM LEAK TEST OF THE VALVE AND ENSURE THAT VALVE CONFORMS TO THE DESIGN VALVE LEAKAGE CLASSIFICATION AS SET OUT IN THE VALVE TAG PLATE OR DATASHEET. ENSURE THE CONTROL VALVE COMPONENTS AND ASSOCIATED CABLING ARE IN GOOD CONDITION, SECURELY FITTED AND FIT FOR PURPOSE. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 36 | MONTH(S)
VALVE, PRESSURE VACCUM RELIEF | TO RELIEF EXCESSIVE PRESSURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF VALVE LEAKAGE IN CLOSED POSITION. | VALVE LEAKAGE IN CLOSED POSITION | CRITICAL | LCP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF VALVE LEAKAGE IN CLOSED POSITION OF PRESSURE RELIEF VALVE {EQUIPMENT TAG NUMBER} EXCEEDS THAN ACCEPTABLE LEAKAGE RATE, SO IT WOULD NOT BE POSSIBLE TO CONTROL THE PROCESS, WHICH RESULT AS PROCESS DISTURBANCE. | LOOSENESS, CORROSION, INSTRUMENT FAILURE-GENERAL | PACKING, SEAT RINGS, SUBUNIT | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 0.38 | 1.16 | 300.3947 | 10 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | MOH | MAJOR OVERHAULING | PERFORM MAJOR OVERHAULING OF THE VALVE, SEAT DISC LAPPING, CLEANING AND SERVICING OF VALVE INTERNALS, AND REPLACEMENT OF ALL SEALS/SOFT GOODS. PERFORM LEAK TEST OF THE VALVE AND ENSURE THAT VALVE CONFORMS TO THE DESIGN VALVE LEAKAGE CLASSIFICATION AS SET OUT IN THE VALVE TAG PLATE OR DATASHEET. ENSURE THE CONTROL VALVE COMPONENTS AND ASSOCIATED CABLING ARE IN GOOD CONDITION, SECURELY FITTED AND FIT FOR PURPOSE. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 36 | MONTH(S)
VALVE, PRESSURE VACCUM RELIEF | TO RELIEF EXCESSIVE PRESSURE OF {SERVICE} FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO REGULATE. | FAIL TO REGULATE | CRITICAL | FTR | AGE/NON-AGE RELATED | EVIDENT | PROCESS AND OPERATIONAL | IF PRESSURE VACCUM RELIEF VALVE {EQUIPMENT TAG NUMBER} FAIL TO REGULATE, IT WOULD NOT BE POSSIBLE TO CONTROL/KEEP THE PROCESS AT A SET POINT, THIS MAY LEADS TO PROCESS DISTURBANCE. | BLOCKAGE/PLUGGED, INSTRUMENT FAILURE-GENERAL | VALVE BODY W/INTERNALS | 4 | F | RISK RANK 4 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.28 | 1.14 | 2.46 | 100.1316 | 2.7 | 3.55 | 11.3 | 22.59 | 10.1018 | 4.2 | 574 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | VISUALLY INSPECT FOR ACTUATOR AND ALL THE TUBING CONNECTIONS FOR UTILITY LEAKAGE AND CHECK POSITIONER FEEDBACK LINK FOR LOOSENESS. ENSURE THAT PROPER INSTRUMENT AIR SUPPLY IS PROVIDING TO POSITIONER AND ACTUATOR AS PER DATA SHEET. ENSURE THAT STEM COUPLING (STEM CONNECTOR) OF ACTUATOR AND VALVE BODY IS TIGHTENED AND PROPERLY ADJUSTED. PERFORM LUBRICATION OF VALVE AND GEARBOX(IF PRESENT). CHECK VALVE TRAVEL IS SAME AS VALVE DATA PLATE. IF THE VALVE STEM TRAVEL INDICATION DIDN’T SHOW CORRECTLY 0% OR 100% TRAVEL AND ANY OFFSET FOUND, PERFORM CALIBRATION OF THE VALVE. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 12 | MONTH(S)
VALVE, EMERGENCY SHUTDOWN | TO STOP THE FLOW OF A {SERVICE} IN THE EVENT/CASE OF AN EMERGENCY FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-PROCESS MEDIUM. | EXTERNAL LEAKAGE-PROCESS MEDIUM | CRITICAL | ELP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | EXTERNAL LEAKAGE OF {SERVICE} FROM EMERGENCY SHUTDOWN VALVE {EQUIPMENT TAG NUMBER} MOUNTED ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} LINE WILL LEAD TO SAFETY HAZARDS AND ENVIRONMENTAL EFFECTS, EXCESSIVE LEAKAGE CAN CAUSE PROCESS INTERRUPTION. | CORROSION, LEAKAGE, MECHANICAL FAILURE-GENERAL | BONNET, SEAT RINGS, STEM, SUBUNIT, PACKING, SEALS | 4 | C | RISK RANK 2 | 4 | C | RISK RANK 2 | 4 | C | RISK RANK 2 | 4 | C | RISK RANK 2 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | 0.05 | 1.12 | 3.37 | 101.9194 | 32 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | PERFORM NECESSARY REPLACEMENTS/ACTION TO MITIGATE THE LEAKAGE. REPLACE CONSUMABLES LIKE GASKETS, O RINGS ETC. CHECK FOR LOOSENESS OR LEAKAGE FROM ACTUATOR OR CONTROL TUBINGS. PERFORM LUBRICATION OF VALVE AND GEARBOX(IF PRESENT). CHECK FOR THE INTERLOCKS OF VALVE OPERATION IF ANY. (FOR DETAILS REFER PMR). | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 48 | MONTH(S)
VALVE, EMERGENCY SHUTDOWN | TO STOP THE FLOW OF A {SERVICE} IN THE EVENT/CASE OF AN EMERGENCY FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-UTILITY MEDIUM. | EXTERNAL LEAKAGE-UTILITY MEDIUM | DEGRADED | ELU | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | EXTERNAL LEAKAGE-UTILITY MEDIUM FROM EMERGENCY SHUTDOWN VALVE {EQUIPMENT TAG NUMBER} MOUNTED ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} LINE CAN LEAD TO THE ABRUPT/UNWANTED CHANGE IN THE VALVE STATE AND THUS LIMITING THE VALVE TO PERFORM TASK EFFICIENTLY. | LEAKAGE, MECHANICAL FAILURE-GENERAL | SEALS, SEALS GASKET | 4 | C | RISK RANK 2 | 4 | C | RISK RANK 2 | 4 | C | RISK RANK 2 | 4 | C | RISK RANK 2 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | 0.004 | 0.24 | 0.76 | 475.425 | 2 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | PERFORM NECESSARY REPLACEMENTS/ACTION TO MITIGATE THE LEAKAGE. REPLACE CONSUMABLES LIKE GASKETS, O RINGS ETC. CHECK FOR LOOSENESS OR LEAKAGE FROM ACTUATOR OR CONTROL TUBINGS. PERFORM LUBRICATION OF VALVE AND GEARBOX(IF PRESENT). CHECK FOR THE INTERLOCKS OF VALVE OPERATION IF ANY. (FOR DETAILS REFER PMR). | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 48 | MONTH(S)
VALVE, EMERGENCY SHUTDOWN | TO STOP THE FLOW OF A {SERVICE} IN THE EVENT/CASE OF AN EMERGENCY FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF VALVE LEAKAGE IN CLOSED POSITION. | VALVE LEAKAGE IN CLOSED POSITION | CRITICAL | LCP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | LEAKAGE IN CLOSED POSITION OF {SERVICE} FROM EMERGENCY SHUTDOWN VALVE {EQUIPMENT TAG NUMBER} MOUNTED ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} LINE MAY CAUSE DOWNTIME AND PROCESS DISTURBANCE. | LEAKAGE, WEAR | VALVE BODY, SEAT | 4 | C | RISK RANK 2 | 4 | C | RISK RANK 2 | 4 | C | RISK RANK 2 | 4 | C | RISK RANK 2 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | - | 0.34 | 1.88 | 335.7353 | - | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CHECK THE INTEGRITY OF ALL THE ASSOCIATED INSTRUMENTATION SUCH AS LIMIT SWITCHES AND SOLENOID VALVES. CHECK THE LIMIT OR POSITION SWITCH FUNCTIONALITY BY USING MULTIMETER. CHECK FOR LOOSENESS OR LEAKAGE FROM ACTUATOR OR CONTROL TUBINGS. PERFORM LUBRICATION OF VALVE AND GEARBOX(IF PRESENT). CHECK FOR THE INTERLOCKS OF VALVE OPERATION IF ANY. (FOR DETAILS REFER PMR). | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 48 | MONTH(S)
VALVE, EMERGENCY SHUTDOWN | TO STOP THE FLOW OF A {SERVICE} IN THE EVENT/CASE OF AN EMERGENCY FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO CLOSE ON DEMAND. | FAIL TO CLOSE ON DEMAND | CRITICAL | FTC | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF EMERGENCY SHUTDOWN VALVE {EQUIPMENT TAG NUMBER} FAIL TO CLOSE ON DEMAND, IT WOULD NOT BE POSSIBLE TO CONTROL THE PROCESS AND THIS MAY LEAD TO PROCESS DISTURBANCE AND THE PRODUCTION LOSS. | BLOCKAGE/PLUGGED, STICKING, INSTRUMENT FAILURE-GENERAL, MECHANICAL FAILURE-GENERAL | VALVE BODY W/INTERNALS, PILOT VALVE, STEM, SUBUNIT, SEAT RINGS | 5 | D | RISK RANK 2 | 5 | D | RISK RANK 2 | 5 | D | RISK RANK 2 | 5 | E | RISK RANK 3 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | - | 2.27 | 11.88 | 50.2863 | 2.8 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CHECK THE INTEGRITY OF ALL THE ASSOCIATED INSTRUMENTATION SUCH AS LIMIT SWITCHES AND SOLENOID VALVES. CHECK THE LIMIT OR POSITION SWITCH FUNCTIONALITY BY USING MULTIMETER. CHECK FOR LOOSENESS OR LEAKAGE FROM ACTUATOR OR CONTROL TUBINGS. PERFORM LUBRICATION OF VALVE AND GEARBOX(IF PRESENT). CHECK FOR THE INTERLOCKS OF VALVE OPERATION IF ANY. (FOR DETAILS REFER PMR). | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 48 | MONTH(S)
VALVE, EMERGENCY SHUTDOWN | TO STOP THE FLOW OF A {SERVICE} IN THE EVENT/CASE OF AN EMERGENCY FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO OPEN ON DEMAND. | FAIL TO OPEN ON DEMAND | CRITICAL | FTO | AGE/NON-AGE RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | IF EMERGENCY SHUTDOWN VALVE {EQUIPMENT TAG NUMBER} FAIL TO OPEN ON DEMAND, IT MAY POSE HAZARD TO THE PROCESS SAFETY AND ENVIRONMENT. THIS MAY LEAD TO SEVERE EQUIPMENT DAMAGE. | BLOCKAGE/PLUGGED, INSTRUMENT FAILURE-GENERAL, MECHANICAL FAILURE-GENERAL | PILOT VALVE, SUBUNIT | 4 | C | RISK RANK 2 | 4 | E | RISK RANK 3 | 4 | C | RISK RANK 2 | 4 | E | RISK RANK 3 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | 0.01 | 1.08 | 3.46 | 105.4944 | 2.3 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CHECK THE INTEGRITY OF ALL THE ASSOCIATED INSTRUMENTATION SUCH AS LIMIT SWITCHES AND SOLENOID VALVES. ENSURE FOR PROPER SUPPLY VOLTAGES TO SOLENOID VALVE. CHECK FOR LOOSENESS OR LEAKAGE FROM ACTUATOR OR CONTROL TUBINGS. ENSURE PROPER WORKING OF ASSOCIATED INSTRUMENTATION OF ESDV. PERFORM LUBRICATION OF VALVE AND GEARBOX(IF PRESENT). CHECK FOR THE INTERLOCKS OF VALVE IF ANY. (FOR DETAILS REFER PMR). | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 48 | MONTH(S)
VALVE, EMERGENCY SHUTDOWN | TO STOP THE FLOW OF A {SERVICE} IN THE EVENT/CASE OF AN EMERGENCY FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF EMERGENCY SHUTDOWN VALVE {EQUIPMENT TAG NUMBER} MOUNTED ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} LINE MAY POSE PROCESS SAFETY HAZARDS AND ENVIRONMENTAL EFFECTS. THIS MAY LEAD TO PROCESS DISTURBANCE. | MECHANICAL FAILURE-GENERAL | SUBUNIT | 4 | C | RISK RANK 2 | 4 | E | RISK RANK 3 | 4 | C | RISK RANK 2 | 4 | E | RISK RANK 3 | RISK RANK 2 | RISK RANK 2 (INTOLERABLE) | - | 0.28 | 1.4 | 407.4786 | 6 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CHECK FOR THE INTERLOCKS OF VALVE OPERATION IF ANY. ENSURE THE VALVE COMPONENTS AND ASSOCIATED CABLING, PIPING ETC. ARE IN GOOD CONDITION, SECURELY FITTED, NOT LEAKING AND FIT FOR PURPOSE. CHECK ALL THE ACCESSORIES FOR DAMAGE OR DEGRADATION. CHECK THE INTEGRITY OF ACCESSORIES FOR PROPER FUNCTIONING. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 48 | MONTH(S)
VALVE, SHUTDOWN | TO STOP THE FLOW OF A {SERVICE} UPON THE DETECTION OF A PROCESS DEFINED EVENT FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-PROCESS MEDIUM. | EXTERNAL LEAKAGE-PROCESS MEDIUM | CRITICAL | ELP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | EXTERNAL LEAKAGE OF {SERVICE} FROM SHUTDOWN VALVE {EQUIPMENT TAG NUMBER} MOUNTED ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} LINE WILL LEAD TO SAFETY HAZARDS AND ENVIRONMENTAL EFFECTS, EXCESSIVE LEAKAGE CAN CAUSE PROCESS INTERRUPTION. | CORROSION, LEAKAGE, MECHANICAL FAILURE-GENERAL | BONNET, SEAT RINGS, STEM, SUBUNIT, PACKING, SEALS | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.05 | 1.12 | 3.37 | 101.9194 | 32 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENT/ACTION TO MITIGATE THE LEAKAGE. CHECK FOR BOLTS TIGHTNESS. REPLACE CONSUMABLES LIKE GASKETS, O-RINGS ETC. (FOR DETAIL, REFER TO PMR) | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, SHUTDOWN | TO STOP THE FLOW OF A {SERVICE} UPON THE DETECTION OF A PROCESS DEFINED EVENT FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF EXTERNAL LEAKAGE-UTILITY MEDIUM. | EXTERNAL LEAKAGE-UTILITY MEDIUM | DEGRADED | ELU | NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | EXTERNAL LEAKAGE-UTILITY MEDIUM FROM SHUTDOWN VALVE {EQUIPMENT TAG NUMBER} MOUNTED ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} LINE CAN LEAD TO THE ABRUPT/UNWANTED CHANGE IN THE VALVE STATE AND THUS LIMITING THE VALVE TO PERFORM TASK EFFICIENTLY. | LEAKAGE, MECHANICAL FAILURE-GENERAL | SEALS, SEALS GASKET | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.004 | 0.24 | 0.76 | 475.425 | 2 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | RTF | RUN TO FAILURE | PERFORM NECESSARY REPLACEMENTS/ACTION TO MITIGATE THE LEAKAGE. REPLACE CONSUMABLES LIKE GASKETS, O RINGS ETC. (FOR DETAIL, REFER TO PMR) | RTF-RUN TO FAILURE | CT-CORRECTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | - | -
VALVE, SHUTDOWN | TO STOP THE FLOW OF A {SERVICE} UPON THE DETECTION OF A PROCESS DEFINED EVENT FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | PARTIAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF VALVE LEAKAGE IN CLOSED POSITION. | VALVE LEAKAGE IN CLOSED POSITION | CRITICAL | LCP | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | LEAKAGE IN CLOSED POSITION OF {SERVICE} FROM SHUTDOWN VALVE {EQUIPMENT TAG NUMBER} MOUNTED ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} LINE MAY CAUSE DOWNTIME AND PROCESS DISTURBANCE. | LEAKAGE, WEAR | VALVE BODY, SEAT | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | 0.34 | 1.88 | 335.7353 | - | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CHECK THE INTEGRITY OF ALL THE ASSOCIATED INSTRUMENTATION SUCH AS LIMIT SWITCHES AND SOLENOID VALVES. CHECK THE LIMIT OR POSITION SWITCH FUNCTIONALITY BY USING MULTIMETER. CHECK FOR LOOSENESS OR LEAKAGE FROM ACTUATOR OR CONTROL TUBINGS. PERFORM LUBRICATION OF VALVE AND GEARBOX(IF PRESENT). CHECK FOR THE INTERLOCKS OF VALVE OPERATION IF ANY. (FOR DETAILS REFER PMR). | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 18 | MONTH(S)
VALVE, SHUTDOWN | TO STOP THE FLOW OF A {SERVICE} UPON THE DETECTION OF A PROCESS DEFINED EVENT FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO CLOSE ON DEMAND. | FAIL TO CLOSE ON DEMAND | CRITICAL | FTC | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF SHUTDOWN VALVE {EQUIPMENT TAG NUMBER} FAIL TO CLOSE ON DEMAND, IT WOULD NOT BE POSSIBLE TO CONTROL THE PROCESS AND THIS MAY LEAD TO PROCESS DISTURBANCE AND THE PRODUCTION LOSS. | BLOCKAGE/PLUGGED, STICKING, INSTRUMENT FAILURE-GENERAL, MECHANICAL FAILURE-GENERAL | VALVE BODY W/INTERNALS, PILOT VALVE, STEM, SUBUNIT, SEAT RINGS | 5 | E | RISK RANK 3 | 5 | E | RISK RANK 3 | 5 | E | RISK RANK 3 | 5 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | 2.27 | 11.88 | 50.2863 | 2.8 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CHECK THE INTEGRITY OF ALL THE ASSOCIATED INSTRUMENTATION SUCH AS LIMIT SWITCHES AND SOLENOID VALVES. CHECK THE LIMIT OR POSITION SWITCH FUNCTIONALITY BY USING MULTIMETER. CHECK FOR LOOSENESS OR LEAKAGE FROM ACTUATOR OR CONTROL TUBINGS. PERFORM LUBRICATION OF VALVE AND GEARBOX(IF PRESENT). CHECK FOR THE INTERLOCKS OF VALVE OPERATION IF ANY. (FOR DETAILS REFER PMR). | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 18 | MONTH(S)
VALVE, SHUTDOWN | TO STOP THE FLOW OF A {SERVICE} UPON THE DETECTION OF A PROCESS DEFINED EVENT FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO OPEN ON DEMAND. | FAIL TO OPEN ON DEMAND | CRITICAL | FTO | AGE/NON-AGE RELATED | HIDDEN | FUNCTIONAL AND PERFORMANCE | IF SHUTDOWN VALVE {EQUIPMENT TAG NUMBER} FAIL TO OPEN ON DEMAND, IT MAY POSE HAZARD TO THE PROCESS SAFETY AND ENVIRONMENT. THIS MAY LEAD TO SEVERE EQUIPMENT DAMAGE. | BLOCKAGE/PLUGGED, INSTRUMENT FAILURE-GENERAL, MECHANICAL FAILURE-GENERAL | PILOT VALVE, SUBUNIT | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | 0.01 | 1.08 | 3.46 | 105.4944 | 2.3 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CHECK THE INTEGRITY OF ALL THE ASSOCIATED INSTRUMENTATION SUCH AS LIMIT SWITCHES AND SOLENOID VALVES. ENSURE FOR PROPER SUPPLY VOLTAGES TO SOLENOID VALVE. CHECK FOR LOOSENESS OR LEAKAGE FROM ACTUATOR OR CONTROL TUBINGS. ENSURE PROPER WORKING OF ASSOCIATED INSTRUMENTATION OF SDV. PERFORM LUBRICATION OF VALVE AND GEARBOX(IF PRESENT). CHECK FOR THE INTERLOCKS OF VALVE IF ANY. (FOR DETAILS REFER PMR). | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 18 | MONTH(S)
VALVE, SHUTDOWN | TO STOP THE FLOW OF A {SERVICE} UPON THE DETECTION OF A PROCESS DEFINED EVENT FOR {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER}. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | SPURIOUS OPERATION OF SHUTDOWN VALVE {EQUIPMENT TAG NUMBER} MOUNTED ON {PARENT TAG DESCRIPTION}{PARENT TAG NUMBER} LINE MAY POSE PROCESS SAFETY HAZARDS AND ENVIRONMENTAL EFFECTS. THIS MAY LEAD TO PROCESS DISTURBANCE. | MECHANICAL FAILURE-GENERAL | SUBUNIT | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | 0.28 | 1.4 | 407.4786 | 6 | 3.82 | 25.08 | 61.92 | 4.5514 | 8.4 | 526 (OREDA 2009) | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CHECK FOR THE INTERLOCKS OF VALVE OPERATION IF ANY. ENSURE THE VALVE COMPONENTS AND ASSOCIATED CABLING, PIPING ETC. ARE IN GOOD CONDITION, SECURELY FITTED, NOT LEAKING AND FIT FOR PURPOSE. CHECK ALL THE ACCESSORIES FOR DAMAGE OR DEGRADATION. CHECK THE INTEGRITY OF ACCESSORIES FOR PROPER FUNCTIONING. (FOR DETAIL, REFER TO PMR) | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 18 | MONTH(S)
MANUAL CALL POINT | TO TRANSFER AN ALARM SIGNAL, AND OPERATE BY MEANS OF A SIMPLE BUTTON PRESS OR WHEN GLASS IS BROKEN REVEALING A BUTTON. THEY CAN FORM PART OF A MANUAL ALARM SYSTEM OR AN AUTOMATIC ALARM SYSTEM. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF MANUAL CALL POINT {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND, THEN ALARM SIGNAL WILL NOT INITIATE. AS A RESULT, ANY PERSONAL FATAL MAY OCCUR AND INTEGRITY OF PLANT WILL EFFECT. | HIGH RESISTANCE IN CONTACTS, OPEN CIRCUIT, FAULTY | PUSH BUTTON | 4 | E | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CHECK THAT THE PUSH BUTTON MANUAL CALL POINT IS IN GOOD CONDITION/NO PHYSICAL DAMAGE AND FREE FROM DIRT/CONTAMINANTS, OBSTRUCTIONS OR SALT ACCUMULATION AND ANY SPLASH OF WATER ETC. IF REQUIRED CLEAN AS NECESSARY CHECK CABLE GLANDS AND EARTH CONNECTIONS FOR DAMAGE AND SECURITY. INSPECT WIRING FOR CRACKED, BROKEN, OR DETERIORATED INSULATION AND EXPOSED CONDUCTOR. CHECK FOR LOOSENESS OF THE HOUSING COVER AND TERMINAL BOX AND CONDUIT PIPE. THE DEVICE MUST CONFORM TO THE AREA CLASSIFICATION. PERFORM FUNCTIONAL TEST OF THE PUSH BUTTON MANUAL CALL POINT BY THE TEST KEY AND PULLING DOWN OR BY PRESSING THE PUSH BUTTON OR BY BREAK GLASS AS APPLICABLE | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 3 | MONTH(S)
MANUAL CALL POINT | TO TRANSFER AN ALARM SIGNAL, AND OPERATE BY MEANS OF A SIMPLE BUTTON PRESS OR WHEN GLASS IS BROKEN REVEALING A BUTTON. THEY CAN FORM PART OF A MANUAL ALARM SYSTEM OR AN AUTOMATIC ALARM SYSTEM. | TOTAL FAILURE OF THE EQUIPMENT OCCUR IN CASE OF SPURIOUS OPERATION. | SPURIOUS OPERATION | CRITICAL | SPO | AGE/NON-AGE RELATED | HIDDEN | PROCESS AND OPERATIONAL | DUE TO SPURIOUS OPERATION OF MANUAL CALL POINT {EQUIPMENT TAG NUMBER}, TOTAL FAILURE OF ALARM WILL OCCUR. DUE TO FAILURE ANY PERSONAL FATAL MAY HAPPEN. | WATER INVASION, SHORT CIRCUIT | PUSH BUTTON | 4 | D | RISK RANK 3 | 4 | D | RISK RANK 3 | 4 | E | RISK RANK 3 | 4 | E | RISK RANK 3 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | INSP | INSPECTION AND FUNCTION TEST | CHECK THAT THE PUSH BUTTON MANUAL CALL POINT IS IN GOOD CONDITION/NO PHYSICAL DAMAGE AND FREE FROM DIRT/CONTAMINANTS, OBSTRUCTIONS OR SALT ACCUMULATION AND ANY SPLASH OF WATER ETC. IF REQUIRED CLEAN AS NECESSARY CHECK CABLE GLANDS AND EARTH CONNECTIONS FOR DAMAGE AND SECURITY. INSPECT WIRING FOR CRACKED, BROKEN, OR DETERIORATED INSULATION AND EXPOSED CONDUCTOR. CHECK FOR LOOSENESS OF THE HOUSING COVER AND TERMINAL BOX AND CONDUIT PIPE. THE DEVICE MUST CONFORM TO THE AREA CLASSIFICATION. PERFORM FUNCTIONAL TEST OF THE PUSH BUTTON MANUAL CALL POINT BY THE TEST KEY AND PULLING DOWN OR BY PRESSING THE PUSH BUTTON OR BY BREAK GLASS AS APPLICABLE | INSP-INSPECTION TASK | INSP-INSPECTION TASK | MAINT-MAINTENANCE TECHNICIAN | ON | 3 | MONTH(S)
ALARM, AUDIBLE | TO WARN/INFORM THE EMPLOYESS FOR EMERGENCY SITUATION AND SAFETY OF THE PERSONNEL PRESENT IN THE PREMISES. | TOTAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF ALARM {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND THEN NO WARNING TO THE PEOPLE FOR EMERGENCY SITUATION AND WILL RESULT IN SAFETY HAZARD TO THE PERSONNEL PRESENT IN THE PREMISES. | HORN FAULTY | HORN | 3 | C | RISK RANK 3 | 3 | E | RISK RANK 4 | 3 | E | RISK RANK 4 | 3 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | VISUALLY INSPECT FOR VISIBLE DAMAGE AND CLEAN, ACCUMULATION OF DUST, DIRT AND SALT AS REQUIRED. CHECK SEALS, GASKETS, GLANDS AND FIXING BOLTS ARE TIGHT AND ALL UNUSED ENTRIES ARE PLUGGED. CHECK FOR CORROSION. TEST ALARM SPEAKERS AND BEACONS BY FORCING THE OUTPUT FROM THE FIRE AND GAS PANEL. CHECK THAT ALL THE ROTATING ALARM BEACONS BEING TESTED ARE WORKING AND FLASHING CORRECTLY. CONFIRM THAT THE SPEAKERS ARE WORKING AND AUDIO IS LOUD AND CLEAR. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 3 | MONTH(S)
ALARM, AUDIBLE | TO WARN/INFORM THE EMPLOYESS FOR EMERGENCY SITUATION AND SAFETY OF THE PERSONNEL PRESENT IN THE PREMISES. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF ERRATIC OUTPUT. | ERRATIC OUTPUT | CRITICAL | ERO | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | ERRATIC OUTPUT OF ALARM {EQUIPMENT TAG NUMBER} MAY RESULT IN IMPROPER INDICATION OF A HAZARDOUS SITUATION, THIS WILL CAUSE SAFETY HAZARD. | COIL FAULTY | COIL | 2 | C | RISK RANK 3 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | VISUALLY INSPECT FOR VISIBLE DAMAGE AND CLEAN, ACCUMULATION OF DUST, DIRT AND SALT AS REQUIRED CHECK SEALS, GASKETS, GLANDS AND FIXING BOLTS ARE TIGHT AND ALL UNUSED ENTRIES ARE PLUGGED. CHECK FOR CORROSION. TEST ALARM SPEAKERS AND BEACONS BY FORCING THE OUTPUT FROM THE FIRE AND GAS PANEL. CHECK THAT ALL THE ROTATING ALARM BEACONS BEING TESTED ARE WORKING AND FLASHING CORRECTLY. CONFIRM THAT THE SPEAKERS ARE WORKING AND AUDIO IS LOUD AND CLEAR. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 3 | MONTH(S)
ALARM, INDICATION | TO WARN/INFORM THE EMPLOYESS FOR EMERGENCY SITUATION AND SAFETY OF THE PERSONNEL PRESENT IN THE PREMISES. | TOTAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF ALARM {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND THEN NO WARNING TO THE PEOPLE FOR EMERGENCY SITUATION AND WILL RESULT IN SAFETY HAZARD TO THE PERSONNEL PRESENT IN THE PREMISES. | HORN FAULTY | HORN | 3 | C | RISK RANK 3 | 3 | E | RISK RANK 4 | 3 | E | RISK RANK 4 | 3 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | VISUALLY INSPECT FOR VISIBLE DAMAGE AND CLEAN, ACCUMULATION OF DUST, DIRT AND SALT AS REQUIRED CHECK SEALS, GASKETS, GLANDS AND FIXING BOLTS ARE TIGHT AND ALL UNUSED ENTRIES ARE PLUGGED. CHECK FOR CORROSION. TEST ALARM SPEAKERS AND BEACONS BY FORCING THE OUTPUT FROM THE FIRE AND GAS PANEL. CHECK THAT ALL THE ROTATING ALARM BEACONS BEING TESTED ARE WORKING AND FLASHING CORRECTLY. CONFIRM THAT THE SPEAKERS ARE WORKING AND AUDIO IS LOUD AND CLEAR. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 3 | MONTH(S)
ALARM, INDICATION | TO WARN/INFORM THE EMPLOYESS FOR EMERGENCY SITUATION AND SAFETY OF THE PERSONNEL PRESENT IN THE PREMISES. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF ERRATIC OUTPUT. | ERRATIC OUTPUT | CRITICAL | ERO | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | ERRATIC OUTPUT OF ALARM {EQUIPMENT TAG NUMBER} MAY RESULT IN IMPROPER INDICATION OF A HAZARDOUS SITUATION, THIS WILL CAUSE SAFETY HAZARD. | COIL FAULTY | COIL | 2 | C | RISK RANK 3 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | VISUALLY INSPECT FOR VISIBLE DAMAGE AND CLEAN, ACCUMULATION OF DUST, DIRT AND SALT AS REQUIRED CHECK SEALS, GASKETS, GLANDS AND FIXING BOLTS ARE TIGHT AND ALL UNUSED ENTRIES ARE PLUGGED. CHECK FOR CORROSION. TEST ALARM SPEAKERS AND BEACONS BY FORCING THE OUTPUT FROM THE FIRE AND GAS PANEL. CHECK THAT ALL THE ROTATING ALARM BEACONS BEING TESTED ARE WORKING AND FLASHING CORRECTLY. CONFIRM THAT THE SPEAKERS ARE WORKING AND AUDIO IS LOUD AND CLEAR. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 3 | MONTH(S)
ALARM, INDICATION HIGH | TO WARN/INFORM THE EMPLOYESS FOR EMERGENCY SITUATION AND SAFETY OF THE PERSONNEL PRESENT IN THE PREMISES. | TOTAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF ALARM {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND THEN NO WARNING TO THE PEOPLE FOR EMERGENCY SITUATION AND WILL RESULT IN SAFETY HAZARD TO THE PERSONNEL PRESENT IN THE PREMISES. | HORN FAULTY | HORN | 3 | C | RISK RANK 3 | 3 | E | RISK RANK 4 | 3 | E | RISK RANK 4 | 3 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | VISUALLY INSPECT FOR VISIBLE DAMAGE AND CLEAN, ACCUMULATION OF DUST, DIRT AND SALT AS REQUIRED CHECK SEALS, GASKETS, GLANDS AND FIXING BOLTS ARE TIGHT AND ALL UNUSED ENTRIES ARE PLUGGED. CHECK FOR CORROSION. TEST ALARM SPEAKERS AND BEACONS BY FORCING THE OUTPUT FROM THE FIRE AND GAS PANEL. CHECK THAT ALL THE ROTATING ALARM BEACONS BEING TESTED ARE WORKING AND FLASHING CORRECTLY. CONFIRM THAT THE SPEAKERS ARE WORKING AND AUDIO IS LOUD AND CLEAR. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 3 | MONTH(S)
ALARM, INDICATION HIGH | TO WARN/INFORM THE EMPLOYESS FOR EMERGENCY SITUATION AND SAFETY OF THE PERSONNEL PRESENT IN THE PREMISES. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF ERRATIC OUTPUT. | ERRATIC OUTPUT | CRITICAL | ERO | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | ERRATIC OUTPUT OF ALARM {EQUIPMENT TAG NUMBER} MAY RESULT IN IMPROPER INDICATION OF A HAZARDOUS SITUATION, THIS WILL CAUSE SAFETY HAZARD. | COIL FAULTY | COIL | 2 | C | RISK RANK 3 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | VISUALLY INSPECT FOR VISIBLE DAMAGE AND CLEAN, ACCUMULATION OF DUST, DIRT AND SALT AS REQUIRED CHECK SEALS, GASKETS, GLANDS AND FIXING BOLTS ARE TIGHT AND ALL UNUSED ENTRIES ARE PLUGGED. CHECK FOR CORROSION. TEST ALARM SPEAKERS AND BEACONS BY FORCING THE OUTPUT FROM THE FIRE AND GAS PANEL. CHECK THAT ALL THE ROTATING ALARM BEACONS BEING TESTED ARE WORKING AND FLASHING CORRECTLY. CONFIRM THAT THE SPEAKERS ARE WORKING AND AUDIO IS LOUD AND CLEAR. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 3 | MONTH(S)
ALARM, MULTIVARIABLE | TO WARN/INFORM THE EMPLOYESS FOR EMERGENCY SITUATION AND SAFETY OF THE PERSONNEL PRESENT IN THE PREMISES. | TOTAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF ALARM {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND THEN NO WARNING TO THE PEOPLE FOR EMERGENCY SITUATION AND WILL RESULT IN SAFETY HAZARD TO THE PERSONNEL PRESENT IN THE PREMISES. | HORN FAULTY | HORN | 3 | C | RISK RANK 3 | 3 | E | RISK RANK 4 | 3 | E | RISK RANK 4 | 3 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | VISUALLY INSPECT FOR VISIBLE DAMAGE AND CLEAN, ACCUMULATION OF DUST, DIRT AND SALT AS REQUIRED. CHECK SEALS, GASKETS, GLANDS AND FIXING BOLTS ARE TIGHT AND ALL UNUSED ENTRIES ARE PLUGGED. CHECK FOR CORROSION. TEST ALARM SPEAKERS AND BEACONS BY FORCING THE OUTPUT FROM THE FIRE AND GAS PANEL. CHECK THAT ALL THE ROTATING ALARM BEACONS BEING TESTED ARE WORKING AND FLASHING CORRECTLY. CONFIRM THAT THE SPEAKERS ARE WORKING AND AUDIO IS LOUD AND CLEAR. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 3 | MONTH(S)
ALARM, MULTIVARIABLE | TO WARN/INFORM THE EMPLOYESS FOR EMERGENCY SITUATION AND SAFETY OF THE PERSONNEL PRESENT IN THE PREMISES. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF ERRATIC OUTPUT. | ERRATIC OUTPUT | CRITICAL | ERO | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | ERRATIC OUTPUT OF ALARM {EQUIPMENT TAG NUMBER} MAY RESULT IN IMPROPER INDICATION OF A HAZARDOUS SITUATION, THIS WILL CAUSE SAFETY HAZARD. | COIL FAULTY | COIL | 2 | C | RISK RANK 3 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | VISUALLY INSPECT FOR VISIBLE DAMAGE AND CLEAN, ACCUMULATION OF DUST, DIRT AND SALT AS REQUIRED CHECK SEALS, GASKETS, GLANDS AND FIXING BOLTS ARE TIGHT AND ALL UNUSED ENTRIES ARE PLUGGED. CHECK FOR CORROSION. TEST ALARM SPEAKERS AND BEACONS BY FORCING THE OUTPUT FROM THE FIRE AND GAS PANEL. CHECK THAT ALL THE ROTATING ALARM BEACONS BEING TESTED ARE WORKING AND FLASHING CORRECTLY. CONFIRM THAT THE SPEAKERS ARE WORKING AND AUDIO IS LOUD AND CLEAR. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 3 | MONTH(S)
ALARM, PRESSURE | TO WARN/INFORM THE EMPLOYESS FOR EMERGENCY SITUATION AND SAFETY OF THE PERSONNEL PRESENT IN THE PREMISES. | TOTAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF ALARM {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND THEN NO WARNING TO THE PEOPLE FOR EMERGENCY SITUATION AND WILL RESULT IN SAFETY HAZARD TO THE PERSONNEL PRESENT IN THE PREMISES. | HORN FAULTY | HORN | 3 | C | RISK RANK 3 | 3 | E | RISK RANK 4 | 3 | E | RISK RANK 4 | 3 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | VISUALLY INSPECT FOR VISIBLE DAMAGE AND CLEAN, ACCUMULATION OF DUST, DIRT AND SALT AS REQUIRED CHECK SEALS, GASKETS, GLANDS AND FIXING BOLTS ARE TIGHT AND ALL UNUSED ENTRIES ARE PLUGGED. CHECK FOR CORROSION. TEST ALARM SPEAKERS AND BEACONS BY FORCING THE OUTPUT FROM THE FIRE AND GAS PANEL. CHECK THAT ALL THE ROTATING ALARM BEACONS BEING TESTED ARE WORKING AND FLASHING CORRECTLY. CONFIRM THAT THE SPEAKERS ARE WORKING AND AUDIO IS LOUD AND CLEAR. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 3 | MONTH(S)
ALARM, PRESSURE | TO WARN/INFORM THE EMPLOYESS FOR EMERGENCY SITUATION AND SAFETY OF THE PERSONNEL PRESENT IN THE PREMISES. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF ERRATIC OUTPUT. | ERRATIC OUTPUT | CRITICAL | ERO | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | ERRATIC OUTPUT OF ALARM {EQUIPMENT TAG NUMBER} MAY RESULT IN IMPROPER INDICATION OF A HAZARDOUS SITUATION, THIS WILL CAUSE SAFETY HAZARD. | COIL FAULTY | COIL | 2 | C | RISK RANK 3 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | VISUALLY INSPECT FOR VISIBLE DAMAGE AND CLEAN, ACCUMULATION OF DUST, DIRT AND SALT AS REQUIRED CHECK SEALS, GASKETS, GLANDS AND FIXING BOLTS ARE TIGHT AND ALL UNUSED ENTRIES ARE PLUGGED. CHECK FOR CORROSION. TEST ALARM SPEAKERS AND BEACONS BY FORCING THE OUTPUT FROM THE FIRE AND GAS PANEL. CHECK THAT ALL THE ROTATING ALARM BEACONS BEING TESTED ARE WORKING AND FLASHING CORRECTLY. CONFIRM THAT THE SPEAKERS ARE WORKING AND AUDIO IS LOUD AND CLEAR. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 3 | MONTH(S)
ALARM, SOUND | TO WARN/INFORM THE EMPLOYESS FOR EMERGENCY SITUATION AND SAFETY OF THE PERSONNEL PRESENT IN THE PREMISES. | TOTAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF FAIL TO FUNCTION ON DEMAND. | FAIL TO FUNCTION ON DEMAND | CRITICAL | FTF | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | IF ALARM {EQUIPMENT TAG NUMBER} FAIL TO FUNCTION ON DEMAND THEN NO WARNING TO THE PEOPLE FOR EMERGENCY SITUATION AND WILL RESULT IN SAFETY HAZARD TO THE PERSONNEL PRESENT IN THE PREMISES. | HORN FAULTY | HORN | 3 | C | RISK RANK 3 | 3 | E | RISK RANK 4 | 3 | E | RISK RANK 4 | 3 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | VISUALLY INSPECT FOR VISIBLE DAMAGE AND CLEAN, ACCUMULATION OF DUST, DIRT AND SALT AS REQUIRED CHECK SEALS, GASKETS, GLANDS AND FIXING BOLTS ARE TIGHT AND ALL UNUSED ENTRIES ARE PLUGGED. CHECK FOR CORROSION. TEST ALARM SPEAKERS AND BEACONS BY FORCING THE OUTPUT FROM THE FIRE AND GAS PANEL. CHECK THAT ALL THE ROTATING ALARM BEACONS BEING TESTED ARE WORKING AND FLASHING CORRECTLY. CONFIRM THAT THE SPEAKERS ARE WORKING AND AUDIO IS LOUD AND CLEAR. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 3 | MONTH(S)
ALARM, SOUND | TO WARN/INFORM THE EMPLOYESS FOR EMERGENCY SITUATION AND SAFETY OF THE PERSONNEL PRESENT IN THE PREMISES. | PARTIAL FAILURE OF FUNCTION WILL HAPPEN IN CASE OF ERRATIC OUTPUT. | ERRATIC OUTPUT | CRITICAL | ERO | AGE/NON-AGE RELATED | EVIDENT | FUNCTIONAL AND PERFORMANCE | ERRATIC OUTPUT OF ALARM {EQUIPMENT TAG NUMBER} MAY RESULT IN IMPROPER INDICATION OF A HAZARDOUS SITUATION, THIS WILL CAUSE SAFETY HAZARD. | COIL FAULTY | COIL | 2 | C | RISK RANK 3 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | 2 | E | RISK RANK 4 | RISK RANK 3 | RISK RANK 3 (TOLERABLE) | - | - | - | - | - | - | - | - | - | - | - | 2018-11-28 | 2023-11-27 | N | - | - | - | - | - | N | - | - | - | - | PMT | PREVENTIVE MAINTENANCE TASK | VISUALLY INSPECT FOR VISIBLE DAMAGE AND CLEAN, ACCUMULATION OF DUST, DIRT AND SALT AS REQUIRED CHECK SEALS, GASKETS, GLANDS AND FIXING BOLTS ARE TIGHT AND ALL UNUSED ENTRIES ARE PLUGGED. CHECK FOR CORROSION. TEST ALARM SPEAKERS AND BEACONS BY FORCING THE OUTPUT FROM THE FIRE AND GAS PANEL. CHECK THAT ALL THE ROTATING ALARM BEACONS BEING TESTED ARE WORKING AND FLASHING CORRECTLY. CONFIRM THAT THE SPEAKERS ARE WORKING AND AUDIO IS LOUD AND CLEAR. | PMT-PREVENTIVE MAINTENANCE TASK | PT-PREVENTIVE TASK | MAINT-MAINTENANCE TECHNICIAN | OFF | 3 | MONTH(S)